## Cover
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 |  |  |  | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 |  |  |  | Page: 1 of 58
FGS I/O LIST
4 | 22.Feb.2021 | Issued For Construction |  |  | 58 | N.F | SH.H | S.CH
3 | 02.Jan.2017 | Issued For Construction |  |  | 52 | N.F | SH.H | S.CH
2 | 09.Mar.2016 | Issued For Approval |  |  | 46 | N.F | SH.H | S.CH
1 | 25.Jun.2015 | Issued For Approval |  |  | 43 | N.F | B.O | S.CH
0 | 15.Dec.2014 | Issued For Approval |  |  | 25 | N.F | S.CH | H.A.
Rev | Date | Status |  |  | Pages | Prepared | Checked | Approved

## Rev. Index
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O List
Owner Doc No.: ESBR-CI-LST-0005 | [19 empty] | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 | [19 empty] | Page: 2 of 58
| Page no. | Revision |  |  |  |  | Page no. |  | Revision |  |  |  |  | Page no. | Revision |  |  |  |  | Page no. | Revision |  |  |  |  | Page no. | Revision |  |  |  |  | Page no. | Revision
|  | 0 | 1 | 2 | 3 | 4 |  |  | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4
| 1 | x | x | x | x | x | 25 |  | x | x | x |  | x | 49 |  |  |  | x | x | 73 | [5 empty] | 97 | [5 empty] | 121
| 2 | x | x | x | x | x | 26 | 4 |  | x | x |  | x | 50 |  |  |  | x | x | 74 | [5 empty] | 98 | [5 empty] | 122
| 3 | x | x | x |  | x | 27 |  |  | x | x | x | x | 51 |  |  |  | x | x | 75 | [5 empty] | 99 | [5 empty] | 123
| 4 | x | x | x | x | x | 28 |  |  | x | x | x | x | 52 |  |  |  | x | x | 76 | [5 empty] | 100 | [5 empty] | 124
| 5 | x | x | x | x | x | 29 | 4 |  | x | x | x | x | 53 |  |  |  |  | x | 77 | [5 empty] | 101 | [5 empty] | 125
| 6 | x | x | x | x | x | 30 |  |  | x | x | x | x | 54 |  |  |  |  | x | 78 | [5 empty] | 102 | [5 empty] | 126
| 7 | x | x | x | x | x | 31 |  |  | x | x | x | x | 55 |  |  |  |  | x | 79 | [5 empty] | 103 | [5 empty] | 127
| 8 | x | x | x | x | x | 32 | 4 |  | x | x | x | x | 56 |  |  |  |  | x | 80 | [5 empty] | 104 | [5 empty] | 128
| 9 | x | x | x | x | x | 33 |  |  | x | x | x | x | 57 |  |  |  |  | x | 81 | [5 empty] | 105 | [5 empty] | 129
| 10 | x | x | x |  | x | 34 |  |  | x | x | x | x | 58 |  |  |  |  | x | 82 | [5 empty] | 106 | [5 empty] | 130
| 11 | x | x | x |  | x | 35 | 4 |  | x | x |  | x | 59 | [5 empty] | 83 | [5 empty] | 107 | [5 empty] | 131
| 12 | x | x | x |  | x | 36 |  |  | x | x |  | x | 60 | [5 empty] | 84 | [5 empty] | 108 | [5 empty] | 132
| 13 | x | x | x | x | x | 37 |  |  | x | x |  | x | 61 | [5 empty] | 85 | [5 empty] | 109 | [5 empty] | 133
| 14 | x | x | x |  | x | 38 | 4 |  | x | x |  | x | 62 | [5 empty] | 86 | [5 empty] | 110 | [5 empty] | 134
| 15 | x | x | x |  | x | 39 |  |  | x | x |  | x | 63 | [5 empty] | 87 | [5 empty] | 111 | [5 empty] | 135
| 16 | x | x | x | x | x | 40 |  |  | x | x |  | x | 64 | [5 empty] | 88 | [5 empty] | 112 | [5 empty] | 136
| 17 | x | x | x |  | x | 41 | 4 |  | x | x |  | x | 65 | [5 empty] | 89 | [5 empty] | 113 | [5 empty] | 137
| 18 | x | x | x | x | x | 42 |  |  | x | x |  | x | 66 | [5 empty] | 90 | [5 empty] | 114 | [5 empty] | 138
| 19 | x | x | x | x | x | 43 |  |  | x | x |  | x | 67 | [5 empty] | 91 | [5 empty] | 115 | [5 empty] | 139
| 20 | x | x | x |  | x | 44 | 4 |  | x | x |  | x | 68 | [5 empty] | 92 | [5 empty] | 116 | [5 empty] | 140
| 21 | x | x | x |  | x | 45 |  |  |  | x |  | x | 69 | [5 empty] | 93 | [5 empty] | 117 | [5 empty] | 141
| 22 | x | x | x |  | x | 46 |  |  |  | x |  | x | 70 | [5 empty] | 94 | [5 empty] | 118 | [5 empty] | 142
| 23 | x | x | x |  | x | 47 | 4 |  |  |  | x | x | 71 | [5 empty] | 95 | [5 empty] | 119 | [5 empty] | 143
| 24 | x | x | x |  | x | 48 |  |  |  |  | x | x | 72 | [5 empty] | 96 | [5 empty] | 120

## Legend
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 |  |  |  | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 |  |  |  | Page: 3 of 58
LEGEND
| INSTRUMENT LOCATION |  | SYSTEM |  | IO Type
| FIELD ( F) : Field ESD : Emergency Shoutdown System DCS/FCS:Distributed Control System / Fieldbus Control System FGDS : Fire & Gas Detectin System SDC : Shut Down Console MCC : Motor Control System PLC : Programmable Logic Controller ICSS : Integrated Control & Safety System LFAP/FAP: Local Fire Alarm Panel in Buildings GFAP: General Fire Alarm Panel in Fire Brigade MP: FGDS MATRIX Panel OWS: FGDS Operator Workstation CCR: Central Control Room FCR: Finishing Control Room CRR: Central Rack Room FRR: Finishing Rack Room MW : Main workshop WH: Ware House MPF: Matrix Panel Finishing MPP: Matrix Panel Prepration CPR: Chemical Prepration |  | DCS :DCS/FCS Distributed Control System / Fieldbus Control System ESD : Emergency Shoutdown System PLC : Programmable Logic Controller MCC : Motor Control System |  | DI : Discrete Input DIR : Redundant Discrete Input DO : Discrete Output DOR : Redundant Discrete Output AI : Analog Input AIR : Redundant Analog Input AO : Analog Output AOR : Redundant Analog Output SDI : Serial Discrete Input SDO : Serial Discrete Output SAI : Serial Analog Input SAO : Serial Analog Output FRS : Fire Resistant as per IEC 60331 FRT : Flame Retardant as per IEC 60331 IS : Intrinsically Safe NIS : Non Intrinsically Safe AL : Addressable Loop
F & G Devices Tag Numbering
| INDOOR |  | OUTDOOR |  | Function Code
| TTTTT-XXXXS TTTTT: Instrument Name XXXX: Four digits, which are a progressive number in the section (from 0001 to 9999) S :a suffix, which identifies two of more items working in split-range, for example (A or B) |  | TTTTT- LLXXXS TTTTT: Instrument Name LLXXX: progressive absolute number (5 digit), as shown below LL : two digits, which identify the production line and section; XXX : three digits, which are a progressive number in the section (from 001 to 999) S: a suffix, which identifies two of more items working in split-range, for example (A or B) |  | IRGD/P : Point type Flammable Gas Detector IRGD/OP : Open Path type Flammable Gas Detector FD :Flame Detector HD : Heat Detector TGD : Toxic Gas Detector MCP : Manual Call Point UK : Hooter UL : Flashing Light SH : Eye Wash and Shower DV : Deluge Valve

## I-O Summary(1)
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 | [6 empty] | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 | [6 empty] | Page: 4 of 58
| MAIN CONTROL SYSTEM & GFAP | [6 empty] | CENTRAL CONTROL BUILDING
| MAIN FGDS I/O Count | [6 empty] | LFAP-1000 I/O Count
| Redundant /Simplex | I/O Type | I/O |  | With 20% hot Spare |  |  | Redundant /Single | I/O Type | I/O |  | With 20% hot Spare
|  |  | IS | NIS | IS | NIS |  |  |  | IS | NIS | IS | NIS
| Redundant | AI | 0 | 596 | 0 | 715.2 |  | Redundant | AI | 0 | 14 | 0 | 16.8
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 113 | 0 | 135.6 |  |  | DI | 0 | 36 | 0 | 43.2
|  | DO | 0 | 327 | 0 | 392.4 |  |  | DO | 0 | 6 | 0 | 7.2
| Simplex | AI | 0 | 41 | 0 | 49.2 |  | Simplex | AI | 0 | 0 | 0 | 0
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 170 | 0 | 204 |  |  | DI | 0 | 41 | 0 | 49.2
|  | DO | 0 | 368 | 0 | 441.6 |  |  | DO | 0 | 61 | 0 | 73.2
| GFAP (Simplex) | DO | 0 | 211 | 0 | 253.2 |  |  | AL | 0 | 3 | 1 | 4.8
| MOTOR CONTROL CENTER | [6 empty] | FINISHING AREA CONTROL CENTER
| LFAP-2000 I/O Count | [6 empty] | LFAP-3000 I/O Count
| Redundant /Single | I/O Type | I/O |  | With 20% hot Spare |  |  | Redundant /Single | I/O Type | I/O |  | With 20% hot Spare
|  |  | IS | NIS | IS | NIS |  |  |  | IS | NIS | IS | NIS
| Redundant | AI | 0 | 14 | 0 | 16.8 |  | Redundant | AI | 0 | 4 | 0 | 4.8
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 41 | 0 | 49.2 |  |  | DI | 0 | 26 | 0 | 31.2
|  | DO | 0 | 5 | 0 | 6 |  |  | DO | 0 | 4 | 0 | 4.8
| Simplex | AI | 0 | 2 | 0 | 2.4 |  | Simplex | AI | 0 | 0 | 0 | 0
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 42 | 0 | 50.4 |  |  | DI | 0 | 19 | 0 | 22.8
|  | DO | 0 | 59 | 0 | 70.8 |  |  | DO | 0 | 26 | 0 | 31.2
|  | AL | 0 | 2 | 2 | 4.8 |  |  | AL | 0 | 1 | 0 | 1.2
| MAIN WORKSHOP | [6 empty] | MAIN WAREHOUSE
| LFAP-4000 I/O Count | [6 empty] | LFAP-5000 I/O Count
| Redundant /Single | I/O Type | I/O |  | With 20% hot Spare |  |  | Redundant /Single | I/O Type | I/O |  | With 20% hot Spare
|  |  | IS | NIS | IS | NIS |  |  |  | IS | NIS | IS | NIS
| Redundant | AI | 0 | 10 | 0 | 12 |  | Redundant | AI | 0 | 19 | 0 | 22.8
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 11 | 0 | 13.2 |  |  | DI | 0 | 7 | 0 | 8.4
|  | DO | 0 | 4 | 0 | 4.8 |  |  | DO | 0 | 4 | 0 | 4.8
| Simplex | AI | 0 | 2 | 0 | 2.4 |  | Simplex | AI | 0 | 0 | 0 | 0
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 19 | 0 | 22.8 |  |  | DI | 0 | 33 | 0 | 39.6
|  | DO | 0 | 52 | 0 | 62.4 |  |  | DO | 0 | 44 | 0 | 52.8
|  | AL | 0 | 3 | 0 | 3.6 |  |  | AL | 0 | 2 | 0 | 2.4

## I-O Summary (2)
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 | [6 empty] | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 | [6 empty] | Page: 5 of 58
| ADMINISTRATION BUILDING | [6 empty] | FIRE FIGHTING BUILDING
| LFAP-7000 I/O Count | [6 empty] | LFAP-8000 I/O Count
| Redundant /Simplex | I/O Type | I/O |  | With 20% hot Spare |  |  | Redundant /Single | I/O Type | I/O |  | With 20% hot Spare
|  |  | IS | NIS | IS | NIS |  |  |  | IS | NIS | IS | NIS
| Redundant | AI | 0 | 14 | 0 | 16.8 |  | Redundant | AI | 0 | 8 | 0 | 9.6
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 6 | 0 | 7.2 |  |  | DI | 0 | 7 | 0 | 8.4
|  | DO | 0 | 3 | 0 | 3 |  |  | DO | 0 | 3 | 0 | 3.6
| Simplex | AI | 0 | 0 | 0 | 0 |  | Simplex | AI | 0 | 0 | 0 | 0
|  | AO | 0 | 0 | 0 | 0 |  |  | AO | 0 | 0 | 0 | 0
|  | DI | 0 | 20 | 0 | 24 |  |  | DI | 0 | 14 | 0 | 16.8
|  | DO | 0 | 35 | 0 | 42 |  |  | DO | 0 | 35 | 0 | 42
|  | AL | 0 | 5 | 0 | 6 |  |  | AL | 0 | 2 | 0 | 2.4

## Cable Code
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 |  |  |  |  | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 |  |  |  |  | Page: 6 of 58
Cable Code Format: NN C AAA SS RRR F JJ I UU X
| Pos. | Designation | Designation Description | Code | Code Interpretation
| 1 | NN | Number | No. | No. of Cores, Pairs, Triads, Quads, Fibers
| 2 | C | Configuration | C | Core
|  |  |  | P | Pair
|  |  |  | T | Triad
|  |  |  | Q | Quad
|  |  |  | F | Fiber
| 3 | AAA | Cross Section | 1.50 ,2.50,A18 | 1.50 =1.5mm2 , 2.50=2.5mm2, A18= AWG18
| 4 | SS | Screen | 00 | No Individual, No Overal Screen
|  |  |  | 01 | No Individual but Overal Screen
|  |  |  | 10 | Individual but No Overal Screen
|  |  |  | 11 | Individual and Overal Screen
| 5 | RRR | Armour | NAR | Non Armoured
|  |  |  | STA | Steel Tape Armour
|  |  |  | SWA | Steel Wire Armour
|  |  |  | SWB | Steel Wire Braid
| 6 | F | Fire Resistance | R | Flame Retardent
|  |  |  | S | Fire Resistant
| 7 | JJ | Jacket Color | BK | Black
|  |  |  | GY | Gray
|  |  |  | GR | Green
|  |  |  | BL | Blue
|  |  |  | GY | Green/Yellow
|  |  |  | OJ | Orange
|  |  |  | RD | Red
|  |  |  | GO | Gray with Orange stripe
|  |  |  | RB | Red With Blue stripe
|  |  |  | BO | Blue with Orange stripe
| 8 | I | Intrinsic Safety | I | Intrinsically Safe
|  |  |  | N | Non Intrinsically Safe
| 9 | UU | Special Cables | TB | Thermocouple, B
|  |  |  | TE | Thermocouple, E
|  |  |  | TJ | Thermocouple, J
|  |  |  | TK | Thermocouple, K
|  |  |  | TR | Thermocouple, R
|  |  |  | TS | Thermocouple, S
|  |  |  | TT | Thermocouple, T
|  |  |  | FF | Foundation Fieldbus
|  |  |  | ET | Ethernet
|  |  |  | MB | Modbus
|  |  |  | FS | Fiberoptic, Single mode
|  |  |  | FM | Fiberoptic, Multi mode
| 10 | X | Special Requirements |  | Text for special cable requirements
Example:
01 P 150 01 SWA R BK N
Single Pair
1.5 mm²
No Individual but Overal Screen
Steel Wire Armored
Flame Retardent
Black Jacketed
Non Intrinsically Safe

## General Notes
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O LIST
Owner Doc No.: ESBR-CI-LST-0005 |  |  | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4 |  |  | Page: 7 of 58
General Note
Note 1. I.S or N.I.S type of signals, wiring and cabling are highly dependent to manufacturers design and will be finalized with relevant vendor documents. This revision is prepared based on NEC In-House Data and Practice
Note 2. For Fire Brigade a General Fire Alaram Panel (GFAP) has been Considered which is implemented with Remote I/O.
Note 3. Some detectors may require Reset signals. These signals will be considered when vendor data are available.
Note 4. Signals for Workshop will be updated on next revision based on Rev.3 of F&G wiring Diagram for Buildings
Note 5. Signals from Deluge , Safety Showers, HVAC & Clean Agents are not modified and will be kept on hold until vendor data is finalized.

## FGS(process Area)
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O List
Owner Doc No.: ESBR-CI-LST-0005 | [13 empty] | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4
Item No. | Rev | unit | Loop Number | TAG- Number | Service_1 | Service_2 | Description | PID/ F&G Detction Layout | I/O Type | Signal Type | Signal Conn. | Rack Room | Eex | Location | JB No. | TB No. | Cable Type | line no. | Typical Loop (1) | Power Source | Input/Output Contact Activated State Action | Valve Failure Action | Low Range | High Range | Eng Units | High High Trip | High Alarm | Low Alarm | Low Low Trip | Cable Routing No. | Data Sheet no. | Manufa cturer | Model no. | Remark
1 | 3 | 1100 | MCP-11003 | MCP-11003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1100JND91 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
2 | 3 | 1100 | MCP-11002 | MCP-11002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1100JND90 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
3 | 3 | 1100 | MCP-11001 | MCP-11001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1100JND89 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
4 | 3 | 1800 | MCP-18001 | MCP-18001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1800JND80 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
5 | 3 | 1800 | MCP-18002 | MCP-18002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1800JND81 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
6 | 3 | 0000 | MCP-18000 | MCP-1800B |  | MANUAL CALL POINT STATUS LAMP AREA 1800 &1100 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
7 | 3 | 0003 | MCP-18000 | MCP-1800C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP AREA 1800 &1100 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
8 | 2 | 1100 | UK-11001 | UK-11001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
9 | 2 | 1100 | UK-11001 | UK-11001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
10 | 2 | 1100 | UK-11001 | UK-11001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
11 | 4 | 1100 | UL-11001 | UL-11001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
12 | 4 | 1100 | UL-11001 | UL-11001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
13 | 4 | 1100 | UL-11001 | UL-11001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND89 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
14 | 2 | 1100 | UK-11002 | UK-11002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
15 | 2 | 1100 | UK-11002 | UK-11002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
16 | 2 | 1100 | UK-11002 | UK-11002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
17 | 4 | 1100 | UL-11002 | UL-11002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
18 | 4 | 1100 | UL-11002 | UL-11002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
19 | 4 | 1100 | UL-11002 | UL-11002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND90 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
20 | 2 | 1100 | UK-11003 | UK-11003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
21 | 2 | 1100 | UK-11003 | UK-11003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
22 | 2 | 1100 | UK-11003 | UK-11003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
23 | 4 | 1100 | UL-11003 | UL-11003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
24 | 4 | 1100 | UL-11003 | UL-11003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
25 | 4 | 1100 | UL-11003 | UL-11003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1100JND91 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1902 | ESBR-CI-DAS-0030
26 | 2 | 1800 | UK-18001 | UK-18001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
27 | 2 | 1800 | UK-18001 | UK-18001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
28 | 2 | 1800 | UK-18001 | UK-18001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
29 | 4 | 1800 | UL-18001 | UL-18001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
30 | 4 | 1800 | UL-18001 | UL-18001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
31 | 4 | 1800 | UL-18001 | UL-18001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND80 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
32 | 2 | 1800 | UK-18002 | UK-18002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
33 | 2 | 1800 | UK-18002 | UK-18002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
34 | 2 | 1800 | UK-18002 | UK-18002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
35 | 4 | 1800 | UL-18002 | UL-18002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
36 | 4 | 1800 | UL-18002 | UL-18002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
37 | 4 | 1800 | UL-18002 | UL-18002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1800JND81 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
38 | 0 | 1200 | MCP-12004 | MCP-12008 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
39 | 0 | 1200 | MCP-12004 | MCP-12007 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
40 | 0 | 1200 | MCP-12004 | MCP-12006 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
41 | 0 | 1200 | MCP-12004 | MCP-12005 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
38 | 2 | 1200 | MCP-12004 | MCP-12001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
39 | 2 | 1200 | MCP-12004 | MCP-12002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
40 | 3 | 1200 | MCP-12003 | MCP-12003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1200JND82 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
41 | 3 | 1200 | MCP-12004 | MCP-12004 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1200JND83 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
42 | 3 | 0000 | MCP-12000 | MCP-12000B |  | MANUAL CALL POINT STATUS LAMP AREA 1200 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
43 | 3 | 0003 | MCP-12000 | MCP-12000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP AREA 1200 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
44 | 3 | 1200 | MCP-12001 | MCP-12001 | HVAC ROOM | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-1202 | DIR | NIS | FGDS | CRR | d | F | 1200JND80 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
45 | 4 | 1200 | MCP-12002 | MCP-12002 | HVAC ROOM | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-1202 | DIR | NIS | FGDS | CRR | d | F | 1200JND80 | 4 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
46 | 4 | 1200 | MCP-12005 | MCP-12005 |  | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1200JND84 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
47 | 4 | 1200 | MCP-12006 | MCP-12006 | along with UK &UL 12002 | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1200JND81 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
48 | 2 | 1200 | UK-12001 | UK-12001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
49 | 2 | 1200 | UK-12001 | UK-12001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
50 | 2 | 1200 | UK-12001 | UK-12001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
51 | 4 | 1200 | UL-12001 | UL-12001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
52 | 4 | 1200 | UL-12001 | UL-12001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
53 | 4 | 1200 | UL-12001 | UL-12001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND80 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
54 | 2 | 1200 | UK-12002 | UK-12002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
55 | 2 | 1200 | UK-12002 | UK-12002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
56 | 2 | 1200 | UK-12002 | UK-12002C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
57 | 4 | 1200 | UL-12002 | UL-12002A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
58 | 4 | 1200 | UL-12002 | UL-12002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
59 | 4 | 1200 | UL-12002 | UL-12002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND81 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
60 | 2 | 1200 | UK-12003 | UK-12003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
61 | 2 | 1200 | UK-12003 | UK-12003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
62 | 2 | 1200 | UK-12003 | UK-12003C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
63 | 4 | 1200 | UL-12003 | UL-12003A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
64 | 4 | 1200 | UL-12003 | UL-12003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
65 | 4 | 1200 | UL-12003 | UL-12003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND82 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
66 | 2 | 1200 | UK-12004 | UK-12004A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
67 | 2 | 1200 | UK-12004 | UK-12004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
68 | 2 | 1200 | UK-12004 | UK-12004C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
69 | 4 | 1200 | UL-12004 | UL-12004A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
70 | 4 | 1200 | UL-12004 | UL-12004B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
71 | 4 | 1200 | UL-12004 | UL-12004C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND83 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
72 | 4 | 1200 | UK-12005 | UK-12005A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
73 | 4 | 1200 | UK-12005 | UK-12005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
74 | 4 | 1200 | UK-12005 | UK-12005C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
75 | 4 | 1200 | UL-12005 | UL-12005A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
76 | 4 | 1200 | UL-12005 | UL-12005B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
77 | 4 | 1200 | UL-12005 | UL-12005C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1200JND84 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
78 | 2 | 1200 | UK-12006 | UK-12006A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
79 | 2 | 1200 | UK-12006 | UK-12006B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
80 | 2 | 1200 | UK-12006 | UK-12006C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
81 | 2 | 1200 | UL-12006 | UL-12006A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
82 | 2 | 1200 | UL-12006 | UL-12006B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
83 | 2 | 1200 | UL-12006 | UL-12006C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND85 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
84 | 2 | 1200 | UK-12007 | UK-12007A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
85 | 2 | 1200 | UK-12007 | UK-12007B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
86 | 2 | 1200 | UK-12007 | UK-12007C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
87 | 2 | 1200 | UL-12007 | UL-12007A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
88 | 2 | 1200 | UL-12007 | UL-12007B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
89 | 2 | 1200 | UL-12007 | UL-12007C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND86 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
90 | 2 | 1200 | UK-12008 | UK-12008A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
91 | 2 | 1200 | UK-12008 | UK-12008B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
92 | 2 | 1200 | UK-12008 | UK-12008C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
93 | 2 | 1200 | UL-12008 | UL-12008A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
94 | 2 | 1200 | UL-12008 | UL-12008B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
95 | 2 | 1200 | UL-12008 | UL-12008C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1200JND87 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
96 | 2 | 1200 | UK-12009 | UK-12009A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
97 | 2 | 1200 | UK-12009 | UK-12009B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
98 | 2 | 1200 | UK-12009 | UK-12009C | Not used | Not used | HOOTER (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
99 | 2 | 1200 | UL-12009 | UL-12009A | Not used |  | FLASHING LIGHT (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
100 | 2 | 1200 | UL-12009 | UL-12009B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
101 | 2 | 1200 | UL-12009 | UL-12009C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT (HVAC ROOM) | ESBR-HS-LYT-1202 |  |  | FGDS | CRR | d | F | 1200JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1201 | ESBR-CI-DAS-0030
104 | 0 | 1300 | MCP-13001 | MCP-13004 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
105 | 0 | 1300 | MCP-13001 | MCP-13002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
106 | 0 | 1300 | MCP-13001 | MCP-13003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
102 | 3 | 1300 | MCP-13001 | MCP-13001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1300JND87 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
108 | 0 | 2300 | MCP-23001 | MCP-23004 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
109 | 0 | 2300 | MCP-23001 | MCP-23002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
110 | 0 | 2300 | MCP-23001 | MCP-23003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
103 | 3 | 2300 | MCP-23001 | MCP-23001 | Activation of Continues audible alarm |  | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 2300JND87 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
104 | 3 | 0000 | MCP-23000 | MCP-23000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1300 & 2300 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
105 | 3 | 0003 | MCP-23000 | MCP-23000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1300 & 2300 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
106 | 2 | 1300 | UK-13001 | UK-13001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
107 | 2 | 1300 | UK-13001 | UK-13001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
108 | 2 | 1300 | UK-13001 | UK-13001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
109 | 4 | 1300 | UL-13001 | UL-13001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
110 | 4 | 1300 | UL-13001 | UL-13001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
111 | 4 | 1300 | UL-13001 | UL-13001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1300JND87 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
112 | 2 | 1300 | UK-13002 | UK-13002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
113 | 2 | 1300 | UK-13002 | UK-13002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
114 | 2 | 1300 | UK-13002 | UK-13002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
115 | 2 | 1300 | UL-13002 | UL-13002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
116 | 2 | 1300 | UL-13002 | UL-13002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
117 | 2 | 1300 | UL-13002 | UL-13002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
118 | 2 | 1300 | UK-13003 | UK-13003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
119 | 2 | 1300 | UK-13003 | UK-13003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
120 | 2 | 1300 | UK-13003 | UK-13003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
121 | 2 | 1300 | UL-13003 | UL-13003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
122 | 2 | 1300 | UL-13003 | UL-13003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
123 | 2 | 1300 | UL-13003 | UL-13003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
124 | 2 | 1300 | UK-13004 | UK-13004A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
125 | 2 | 1300 | UK-13004 | UK-13004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
126 | 2 | 1300 | UK-13004 | UK-13004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
127 | 2 | 1300 | UL-13004 | UL-13004A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
128 | 2 | 1300 | UL-13004 | UL-13004B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
129 | 2 | 1300 | UL-13004 | UL-13004C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
130 | 2 | 2300 | UK-23001 | UK-23001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
131 | 2 | 2300 | UK-23001 | UK-23001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
132 | 2 | 2300 | UK-23001 | UK-23001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
133 | 4 | 2300 | UL-23001 | UL-23001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
134 | 4 | 2300 | UL-23001 | UL-23001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
135 | 4 | 2300 | UL-23001 | UL-23001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2300JND87 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
136 | 2 | 2300 | UK-23002 | UK-23002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
137 | 2 | 2300 | UK-23002 | UK-23002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
138 | 2 | 2300 | UK-23002 | UK-23002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
139 | 2 | 2300 | UL-23002 | UL-23002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
140 | 2 | 2300 | UL-23002 | UL-23002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
141 | 2 | 2300 | UL-23002 | UL-23002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND88 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
142 | 2 | 2300 | UK-23003 | UK-23003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
143 | 2 | 2300 | UK-23003 | UK-23003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
144 | 2 | 2300 | UK-23003 | UK-23003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
145 | 2 | 2300 | UL-23003 | UL-23003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
146 | 2 | 2300 | UL-23003 | UL-23003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
147 | 2 | 2300 | UL-23003 | UL-23003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND89 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
148 | 2 | 2300 | UK-23004 | UK-23004A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
149 | 2 | 2300 | UK-23004 | UK-23004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
150 | 2 | 2300 | UK-23004 | UK-23004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
151 | 2 | 2300 | UL-23004 | UL-23004A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
152 | 2 | 2300 | UL-23004 | UL-23004B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
153 | 2 | 2300 | UL-23004 | UL-23004C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 2300JND90 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
162 | 0 | 1400 | MCP-14001 | MCP-14004 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
163 | 0 | 1400 | MCP-14001 | MCP-14003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 |  |  |  |  | d | F | [6 empty] | OPEN
154 | 3 | 1400 | MCP-14002 | MCP-14002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1400JND96 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
155 | 3 | 1400 | MCP-14001 | MCP-14001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1400JND95 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
156 | 3 | 0000 | MCP-14000 | MCP-14000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1400 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
157 | 3 | 0003 | MCP-14001 | MCP-14000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1400 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
158 | 2 | 1400 | UK-14001 | UK-14001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
159 | 2 | 1400 | UK-14001 | UK-14001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
160 | 2 | 1400 | UK-14001 | UK-14001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
161 | 4 | 1400 | UL-14001 | UL-14001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
162 | 4 | 1400 | UL-14001 | UL-14001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
163 | 4 | 1400 | UL-14001 | UL-14001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND95 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
164 | 2 | 1400 | UK-14002 | UK-14002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
165 | 2 | 1400 | UK-14002 | UK-14002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
166 | 2 | 1400 | UK-14002 | UK-14002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
167 | 4 | 1400 | UL-14002 | UL-14002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
168 | 4 | 1400 | UL-14002 | UL-14002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
169 | 4 | 1400 | UL-14002 | UL-14002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1400JND96 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
170 | 2 | 1400 | UK-14003 | UK-14003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
171 | 2 | 1400 | UK-14003 | UK-14003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
172 | 2 | 1400 | UK-14003 | UK-14003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
173 | 2 | 1400 | UL-14003 | UL-14003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
174 | 2 | 1400 | UL-14003 | UL-14003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
175 | 2 | 1400 | UL-14003 | UL-14003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND97 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
176 | 2 | 1400 | UK-14004 | UK-14004A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
177 | 2 | 1400 | UK-14004 | UK-14004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
178 | 2 | 1400 | UK-14004 | UK-14004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
179 | 2 | 1400 | UL-14004 | UL-14004A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
180 | 2 | 1400 | UL-14004 | UL-14004B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
181 | 2 | 1400 | UL-14004 | UL-14004C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 |  |  | FGDS | CRR | d | F | 1400JND98 |  | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
182 | 3 | 1500 | MCP-15002 | MCP-15002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 1500JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1501 | ESBR-CI-DAS-0030
183 | 3 | 1500 | MCP-15001 | MCP-15001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 1500JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1501 | ESBR-CI-DAS-0030
184 | 3 | 0000 | MCP-15000 | MCP-15000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1500 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
185 | 3 | 0003 | MCP-15000 | MCP-15000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1500 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
186 | 2 | 1500 | UK-15001 | UK-15001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
187 | 2 | 1500 | UK-15001 | UK-15001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
188 | 2 | 1500 | UK-15001 | UK-15001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
189 | 4 | 1500 | UL-15001 | UL-15001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
190 | 4 | 1500 | UL-15001 | UL-15001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
191 | 4 | 1500 | UL-15001 | UL-15001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
192 | 2 | 1500 | UK-15002 | UK-15002A | AUDIBLE ALARM (CONTINUOUS ) | Shower,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
193 | 2 | 1500 | UK-15002 | UK-15002B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
194 | 2 | 1500 | UK-15002 | UK-15002C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
195 | 4 | 1500 | UL-15002 | UL-15002A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
196 | 4 | 1500 | UL-15002 | UL-15002B | (RED FLASHING LIGHT) | Shower,MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
197 | 4 | 1500 | UL-15002 | UL-15002C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1500JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
198 | 3 | 3600 | MCP-36001 | MCP-36001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 3600JND78 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
199 | 3 | 1600 | MCP-16003 | MCP-16003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 1600JND84 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
200 | 3 | 4600 | MCP-46001 | MCP-46001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 4600JND78 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030
201 | 3 | 4600 | MCP-46002 | MCP-46002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 4600JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030
202 | 3 | 2600 | MCP-26001 | MCP-26001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 2600JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
203 | 3 | 1600 | MCP-16002 | MCP-16002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 1600JND83 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
204 | 3 | 1600 | MCP-16001 | MCP-16001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | FRR | d | F | 1600JND82 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
205 | 3 | 0000 | MCP-16000 | MCP-16000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
206 | 3 | 0003 | MCP-16000 | MCP-16000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
207 | 2 | 1600 | UK-16001 | UK-16001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
208 | 2 | 1600 | UK-16001 | UK-16001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
209 | 2 | 1600 | UK-16001 | UK-16001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
210 | 4 | 1600 | UL-16001 | UL-16001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
211 | 4 | 1600 | UL-16001 | UL-16001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
212 | 4 | 1600 | UL-16001 | UL-16001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND82 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
213 | 2 | 1600 | UK-16002 | UK-16002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
214 | 2 | 1600 | UK-16002 | UK-16002B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
215 | 2 | 1600 | UK-16002 | UK-16002C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
216 | 4 | 1600 | UL-16002 | UL-16002A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
217 | 4 | 1600 | UL-16002 | UL-16002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
218 | 4 | 1600 | UL-16002 | UL-16002C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND83 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
219 | 2 | 1600 | UK-16003 | UK-16003A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
220 | 2 | 1600 | UK-16003 | UK-16003B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
221 | 2 | 1600 | UK-16003 | UK-16003C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
222 | 4 | 1600 | UL-16003 | UL-16003A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
223 | 4 | 1600 | UL-16003 | UL-16003B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
224 | 4 | 1600 | UL-16003 | UL-16003C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 1600JND84 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
225 | 4 | 4600 | UK-46002 | UK-46002A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
226 | 4 | 4600 | UK-46002 | UK-46002B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
227 | 4 | 4600 | UK-46002 | UK-46002C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
228 | 4 | 4600 | UL-46002 | UL-46002A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
229 | 4 | 4600 | UL-46002 | UL-46002B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
230 | 4 | 4600 | UL-46002 | UL-46002C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
231 | 2 | 2600 | UK-26001 | UK-26001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
232 | 2 | 2600 | UK-26001 | UK-26001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
233 | 2 | 2600 | UK-26001 | UK-26001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
234 | 4 | 2600 | UL-26001 | UL-26001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
235 | 4 | 2600 | UL-26001 | UL-26001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
236 | 4 | 2600 | UL-26001 | UL-26001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 2600JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030
237 | 2 | 3600 | UK-36001 | UK-36001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
238 | 2 | 3600 | UK-36001 | UK-36001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
239 | 2 | 3600 | UK-36001 | UK-36001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
240 | 4 | 3600 | UL-36001 | UL-36001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
241 | 4 | 3600 | UL-36001 | UL-36001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
242 | 4 | 3600 | UL-36001 | UL-36001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 3600JND78 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
243 | 2 | 4600 | UK-46001 | UK-46001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
244 | 2 | 4600 | UK-46001 | UK-46001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
245 | 2 | 4600 | UK-46001 | UK-46001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
246 | 4 | 4600 | UL-46001 | UL-46001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
247 | 4 | 4600 | UL-46001 | UL-46001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
248 | 4 | 4600 | UL-46001 | UL-46001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | FRR | d | F | 4600JND78 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
249 | 3 | 1700 | MCP-17001 | MCP-17001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1700JND79 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
250 | 3 | 0000 | MCP-17000 | MCP-17000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1700 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
251 | 3 | 0003 | MCP-17000 | MCP-17000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1700 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
252 | 2 | 1700 | UK-17001 | UK-17001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP,HD,FD | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
253 | 2 | 1700 | UK-17001 | UK-17001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
254 | 2 | 1700 | UK-17001 | UK-17001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
255 | 4 | 1700 | UL-17001 | UL-17001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
256 | 4 | 1700 | UL-17001 | UL-17001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP,HD,FD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
257 | 4 | 1700 | UL-17001 | UL-17001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1700JND79 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
258 | 3 | 1900 | MCP-19001 | MCP-19001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1900JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030
259 | 3 | 1900 | MCP-19002 | MCP-19002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1900JND74 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030
260 | 4 | 1900 | MCP-19003 | MCP-19003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 1900JND76 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030
261 | 3 | 0000 | MCP-19000 | MCP-19000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1900 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
262 | 3 | 0003 | MCP-19000 | MCP-19000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1900 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
263 | 2 | 1900 | UK-19001 | UK-19001A | AUDIBLE ALARM (CONTINUOUS ) | MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
264 | 2 | 1900 | UK-19001 | UK-19001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
265 | 2 | 1900 | UK-19001 | UK-19001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
266 | 4 | 1900 | UL-19001 | UL-19001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
267 | 4 | 1900 | UL-19001 | UL-19001B | (RED FLASHING LIGHT) | MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
268 | 4 | 1900 | UL-19001 | UL-19001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
269 | 2 | 1900 | UK-19002 | UK-19002A | AUDIBLE ALARM (CONTINUOUS ) | MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
270 | 2 | 1900 | UK-19002 | UK-19002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
271 | 2 | 1900 | UK-19002 | UK-19002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
272 | 4 | 1900 | UL-19002 | UL-19002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
273 | 4 | 1900 | UL-19002 | UL-19002B | (RED FLASHING LIGHT) | MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
274 | 4 | 1900 | UL-19002 | UL-19002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
275 | 4 | 1900 | UK-19003 | UK-19003A | AUDIBLE ALARM (CONTINUOUS ) | MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
276 | 4 | 1900 | UK-19003 | UK-19003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
277 | 4 | 1900 | UK-19003 | UK-19003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
278 | 4 | 1900 | UL-19003 | UL-19003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
279 | 4 | 1900 | UL-19003 | UL-19003B | (RED FLASHING LIGHT) | MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
280 | 4 | 1900 | UL-19003 | UL-19003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 1900JND76 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-1001 | ESBR-CI-DAS-0030
281 | 3 | 2100 | MCP-21001 | MCP-21001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 2100JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
282 | 3 | 2100 | MCP-21002 | MCP-21002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0005 | DIR | NIS | FGDS | CRR | d | F | 2100JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
283 | 4 | 0000 | DV-16030 | HS-16701B |  | HAND SWITCH(CONTROL ROOM) 16030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND19 | 1 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
284 | 3 | 0003 | MCP-21000 | MCP-21000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 2100 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
285 | 2 | 2100 | UK-21001 | UK-21001A | AUDIBLE ALARM (CONTINUOUS ) | MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
286 | 2 | 2100 | UK-21001 | UK-21001B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
287 | 2 | 2100 | UK-21001 | UK-21001C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
288 | 4 | 2100 | UL-21001 | UL-21001A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
289 | 4 | 2100 | UL-21001 | UL-21001B | (RED FLASHING LIGHT) | MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
290 | 4 | 2100 | UL-21001 | UL-21001C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
291 | 2 | 2100 | UK-21002 | UK-21002A | AUDIBLE ALARM (CONTINUOUS ) | MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
292 | 2 | 2100 | UK-21002 | UK-21002B | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
293 | 2 | 2100 | UK-21002 | UK-21002C | Not used | Not used | HOOTER | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
294 | 4 | 2100 | UL-21002 | UL-21002A | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
295 | 4 | 2100 | UL-21002 | UL-21002B | (RED FLASHING LIGHT) | MCP | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
296 | 4 | 2100 | UL-21002 | UL-21002C | Not used |  | FLASHING LIGHT | ESBR-HS-LYT-0005 | DO | NIS | FGDS | CRR | d | F | 2100JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-2101 | ESBR-CI-DAS-0030
297 | 1 | 1100 | IRGD-11001 | IRGD/P-11001 | P-1101 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
301 | 0 | 1100 | IRGD-11001 | IRGAH-11001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
302 | 0 | 1100 | IRGD-11001 | IRGAHH-11001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
298 | 3 | 0000 | IRGD-11000 | IRGA-11000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1100&1800 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
299 | 3 | 0003 | IRGD-11000 | IRGA-11000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1100&1800 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
300 | 1 | 1100 | IRGD-11002 | IRGD/P-11002 | P-1103 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
306 | 0 | 1100 | IRGD-11002 | IRGAH-11002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
307 | 0 | 1100 | IRGD-11002 | IRGAHHP11002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
301 | 1 | 1100 | IRGD-11003 | IRGD/P-11003 | P-1111 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
309 | 0 | 1100 | IRGD-11003 | IRGAH-11003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
310 | 0 | 1100 | IRGD-11003 | IRGAHH-11003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
302 | 1 | 1100 | IRGD-11004 | IRGD/P-11004 | P-1109 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
312 | 0 | 1100 | IRGD-11004 | IRGAH-11004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
313 | 0 | 1100 | IRGD-11004 | IRGAHH-11004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
314 | 0 | 1100 | IRGD-11005 | IRGD/P-11005 | P-1130 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
315 | 0 | 1100 | IRGD-11005 | IRGAH-11005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
316 | 0 | 1100 | IRGD-11005 | IRGAHH-11005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
317 | 0 | 1100 | IRGD-11006 | IRGD/P-11006 | S-1101 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
318 | 0 | 1100 | IRGD-11006 | IRGAH-11006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
319 | 0 | 1100 | IRGD-11006 | IRGAHH-11006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
320 | 0 | 1100 | IRGD-11007 | IRGD/P-11007 | S-1102 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
321 | 0 | 1100 | IRGD-11007 | IRGAHP11007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
322 | 0 | 1100 | IRGD-11007 | IRGAHH-11007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
323 | 0 | 1100 | IRGD-11008 | IRGD/P-11008 | P-1134 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
324 | 0 | 1100 | IRGD-11008 | IRGAH-11008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
325 | 0 | 1100 | IRGD-11008 | IRGAHH-11008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
303 | 1 | 1100 | IRGD-11009 | IRGD/P-11009 | V-1101 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
327 | 0 | 1100 | IRGD-11009 | IRGAH-11009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
328 | 0 | 1100 | IRGD-11009 | IRGAHH-11009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
304 | 1 | 1100 | IRGD-11010 | IRGD/P-11010 | V-1102S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
330 | 0 | 1100 | IRGD-11010 | IRGAH-11010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
331 | 0 | 1100 | IRGD-11010 | IRGAHH-11010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
305 | 1 | 1100 | IRGD-11011 | IRGD/P-11011 | V-1102 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
333 | 0 | 1100 | IRGD-11011 | IRGAH-11011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
334 | 0 | 1100 | IRGD-11011 | IRGAHH-11011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
306 | 1 | 1100 | IRGD-11012 | IRGD/P-11012 | V-1103 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
336 | 0 | 1100 | IRGD-11012 | IRGAH-11012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
337 | 0 | 1100 | IRGD-11012 | IRGAHH-11012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
307 | 1 | 1100 | IRGD-11013 | IRGD/P-11013 | V-1103S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
339 | 0 | 1100 | IRGD-11013 | IRGAH-11013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
340 | 0 | 1100 | IRGD-11013 | IRGAHH-11013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
308 | 1 | 1100 | IRGD-11014 | IRGD/P-11014 | V-1104 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
342 | 0 | 1100 | IRGD-11014 | IRGAH-11014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
343 | 0 | 1100 | IRGD-11014 | IRGAHH-11014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
309 | 1 | 1100 | IRGD-11015 | IRGD/P-11015 | V-1115 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
345 | 0 | 1100 | IRGD-11015 | IRGAH-11015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
346 | 0 | 1100 | IRGD-11015 | IRGAHH-11015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
310 | 1 | 1100 | IRGD-11016 | IRGD/P-11016 | E-1104 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
348 | 0 | 1100 | IRGD-11016 | IRGAH-11016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
349 | 0 | 1100 | IRGD-11016 | IRGAHH-11016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
311 | 1 | 1100 | IRGD-11017 | IRGD/P-11017 | V-1116S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
351 | 0 | 1100 | IRGD-11017 | IRGAH-11017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
352 | 0 | 1100 | IRGD-11017 | IRGAHH-11017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
312 | 1 | 1100 | IRGD-11018 | IRGD/P-11018 | V-1116 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
354 | 0 | 1100 | IRGD-11018 | IRGAH-11018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
355 | 0 | 1100 | IRGD-11018 | IRGAH-11018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
313 | 1 | 1100 | IRGD-11019 | IRGD/OPT-11019 | E-1103 & V-1116 | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 |  |  |  |  | d | F
314 | 1 | 1100 | IRGD-11019 | IRGD/OPR-11019 | E-1103 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
358 | 0 | 1100 | IRGD-11019 | IRGAH-11019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
359 | 0 | 1100 | IRGD-11019 | IRGAHH-11019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
315 | 1 | 1100 | IRGD-11020 | IRGD/P-11020 | V-1105A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
361 | 0 | 1100 | IRGD-11020 | IRGAH-11020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
362 | 0 | 1100 | IRGD-11020 | IRGAHH-11020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
316 | 1 | 1100 | IRGD-11021 | IRGD/P-11021 | V-1107A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
364 | 0 | 1100 | IRGD-11021 | IRGAH-11021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
365 | 0 | 1100 | IRGD-11021 | IRGAHH-11021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
317 | 1 | 1100 | IRGD-11022 | IRGD/P-11022 | V-1107B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
367 | 0 | 1100 | IRGD-11022 | IRGAH-11022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
368 | 0 | 1100 | IRGD-11022 | IRGAHH-11022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
318 | 1 | 1100 | IRGD-11023 | IRGD/P-11023 | V-1105B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
370 | 0 | 1100 | IRGD-11023 | IRGAH-11023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
371 | 0 | 1100 | IRGD-11023 | IRGAHH-11023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
319 | 1 | 1100 | IRGD-11024 | IRGD/P-11024 | V-1106A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
373 | 0 | 1100 | IRGD-11024 | IRGAH-11024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
374 | 0 | 1100 | IRGD-11024 | IRGAHH-11024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
320 | 1 | 1100 | IRGD-11025 | IRGD/P-11025 | V-1108A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
376 | 0 | 1100 | IRGD-11025 | IRGAH-11025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
377 | 0 | 1100 | IRGD-11025 | IRGAHH-11025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
321 | 1 | 1100 | IRGD-11026 | IRGD/P-11026 | V-1108B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
379 | 0 | 1100 | IRGD-11026 | IRGAH-11026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
380 | 0 | 1100 | IRGD-11026 | IRGAHH-11026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
322 | 1 | 1100 | IRGD-11027 | IRGD/P-11027 | V-1106B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
382 | 0 | 1100 | IRGD-11027 | IRGAH-11027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
383 | 0 | 1100 | IRGD-11027 | IRGAHH-11027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
323 | 1 | 1100 | IRGD-11028 | IRGD/P-11028 | V-1111 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
385 | 0 | 1100 | IRGD-11028 | IRGAH-11028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
386 | 0 | 1100 | IRGD-11028 | IRGAHH-11028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
324 | 1 | 1100 | IRGD-11029 | IRGD/OPT-11029 | V-1101, V-1102/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 |  |  |  |  | d | F
325 | 1 | 1100 | IRGD-11029 | IRGD/OPR-11029 | V-1101, V-1102/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
326 | 1 | 1100 | IRGD-11029 | IRGAH-11029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
327 | 1 | 1100 | IRGD-11029 | IRGAH-11029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
328 | 1 | 1100 | IRGD-11030 | IRGD/OPT-11030 | V-1103/S, V-1104 | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 |  |  |  |  | d | F
329 | 1 | 1100 | IRGD-11030 | IRGD/OPR-11030 | V-1103/S, V-1104 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
330 | 1 | 1100 | IRGD-11030 | IRGAH-11030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
331 | 1 | 1100 | IRGD-11030 | IRGAH-11030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
332 | 1 | 1100 | IRGD-11031 | IRGD/OPT-11031 | V-1115, V-1116/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 |  |  |  |  | d | F
333 | 1 | 1100 | IRGD-11031 | IRGD/OPR-11031 | V-1115, V-1116/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
334 | 1 | 1100 | IRGD-11031 | IRGAH-11031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
335 | 1 | 1100 | IRGD-11031 | IRGAH-11031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
336 | 1 | 1100 | IRGD-11032 | IRGD/P-11032 | V-1105A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
337 | 1 | 1100 | IRGD-11032 | IRGAH-11032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
338 | 1 | 1100 | IRGD-11032 | IRGAHH-11032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
339 | 1 | 1100 | IRGD-11033 | IRGD/P-11033 | V-1107A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
340 | 1 | 1100 | IRGD-11033 | IRGAH-11033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
341 | 1 | 1100 | IRGD-11033 | IRGAHH-11033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
342 | 1 | 1100 | IRGD-11034 | IRGD/P-11034 | V-1107B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
343 | 1 | 1100 | IRGD-11034 | IRGAH-11034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
344 | 1 | 1100 | IRGD-11034 | IRGAHH-11034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
345 | 1 | 1100 | IRGD-11035 | IRGD/P-11035 | V-1105B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
346 | 1 | 1100 | IRGD-11035 | IRGAH-11035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
347 | 1 | 1100 | IRGD-11035 | IRGAHH-11035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
348 | 1 | 1100 | IRGD-11036 | IRGD/P-11036 | V-1106A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
349 | 1 | 1100 | IRGD-11036 | IRGAH-11036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
350 | 1 | 1100 | IRGD-11036 | IRGAHH-11036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
351 | 1 | 1100 | IRGD-11037 | IRGD/P-11037 | V-1108A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
352 | 1 | 1100 | IRGD-11037 | IRGAH-11037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
353 | 1 | 1100 | IRGD-11037 | IRGAHH-11037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
354 | 1 | 1100 | IRGD-11038 | IRGD/P-11038 | V-1108B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
355 | 1 | 1100 | IRGD-11038 | IRGAH-11038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
356 | 1 | 1100 | IRGD-11038 | IRGAHH-11038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
357 | 1 | 1100 | IRGD-11039 | IRGD/P-11039 | V-1106B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
358 | 1 | 1100 | IRGD-11039 | IRGAH-11039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
359 | 1 | 1100 | IRGD-11039 | IRGAHH-11039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
360 | 1 | 1100 | TGD-11001 | TGD-11001 | P-1101 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
424 | 0 | 1100 | TGD-11001 | TGAH-11001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
425 | 0 | 1100 | TGD-11001 | TGAHH-11001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
361 | 3 | 0000 | TGD-11000 | TGA11000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 1100&1800 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
362 | 3 | 0003 | TGD-11000 | TGA11000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1100&1800 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
363 | 1 | 1100 | TGD-11002 | TGD-11002 | P-1103 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
429 | 0 | 1100 | TGD-11002 | TGAH-11002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
430 | 0 | 1100 | TGD-11002 | TGAHH-11002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
364 | 1 | 1100 | TGD-11003 | TGD-11003 | P-1111 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
432 | 0 | 1100 | TGD-11003 | TGAH-11003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
433 | 0 | 1100 | TGD-11003 | TGAHH-11003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
365 | 1 | 1100 | TGD-11004 | TGD-11004 | P-1109 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
435 | 0 | 1100 | TGD-11004 | TGAH-11004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
436 | 0 | 1100 | TGD-11004 | TGAHH-11004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
437 | 0 | 1100 | TGD-11005 | TGD-11005 | P-1130 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
438 | 0 | 1100 | TGD-11005 | TGAH-11005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
439 | 0 | 1100 | TGD-11005 | TGAHH-11005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
440 | 0 | 1100 | TGD-11006 | TGD-11006 | S-1101 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
441 | 0 | 1100 | TGD-11006 | TGAH-11006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
442 | 0 | 1100 | TGD-11006 | TGAHH-11006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
443 | 0 | 1100 | TGD-11007 | TGD-11007 | S-1102 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
444 | 0 | 1100 | TGD-11007 | TGAH-11007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
445 | 0 | 1100 | TGD-11007 | TGAHH-11007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
446 | 0 | 1100 | TGD-11008 | TGD-11008 | P-1134 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
447 | 0 | 1100 | TGD-11008 | TGAH-11008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
448 | 0 | 1100 | TGD-11008 | TGAHH-11008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
449 | 0 | 1100 | TGD-11009 | TGD-11009 | V-1101 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
450 | 0 | 1100 | TGD-11009 | TGAH-11009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
451 | 0 | 1100 | TGD-11009 | TGAHH-11009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
452 | 0 | 1100 | TGD-11010 | TGD-11010 | V-1102S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
453 | 0 | 1100 | TGD-11010 | TGAH-11010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
454 | 0 | 1100 | TGD-11010 | TGAHH-11010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
455 | 0 | 1100 | TGD-11011 | TGD-11011 | V-1102 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
456 | 0 | 1100 | TGD-11011 | TGAH-11011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
457 | 0 | 1100 | TGD-11011 | TGAHH-11011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
458 | 0 | 1100 | TGD-11012 | TGD-11012 | V-1103 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
459 | 0 | 1100 | TGD-11012 | TGAH-11012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
460 | 0 | 1100 | TGD-11012 | TGAHH-11012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
461 | 0 | 1100 | TGD-11013 | TGD-11013 | V-1103S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA72 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
462 | 0 | 1100 | TGD-11013 | TGAH-11013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
463 | 0 | 1100 | TGD-11013 | TGAHH-11013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
464 | 0 | 1100 | TGD-11014 | TGD-11014 | V-1104 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
465 | 0 | 1100 | TGD-11014 | TGAH-11014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
466 | 0 | 1100 | TGD-11014 | TGAHH-11014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
467 | 0 | 1100 | TGD-11015 | TGD-11015 | V-1115 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
468 | 0 | 1100 | TGD-11015 | TGAH-11015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
469 | 0 | 1100 | TGD-11015 | TGAHH-11015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
470 | 0 | 1100 | TGD-11016 | TGD-11016 | E-1104 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
471 | 0 | 1100 | TGD-11016 | TGAH-11016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
472 | 0 | 1100 | TGD-11016 | TGAHH-11016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
473 | 0 | 1100 | TGD-11017 | TGD-11017 | V-1116S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
474 | 0 | 1100 | TGD-11017 | TGAH-11017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
475 | 0 | 1100 | TGD-11017 | TGAHH-11017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
476 | 0 | 1100 | TGD-11018 | TGD-11018 | V-1116 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
477 | 0 | 1100 | TGD-11018 | TGAH-11018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
478 | 0 | 1100 | TGD-11018 | TGAHH-11018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
479 | 0 | 1100 | TGD-11019 | TGD-11019 | E-1103 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA73 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
480 | 0 | 1100 | TGD-11019 | TGAH-11019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
481 | 0 | 1100 | TGD-11019 | TGAHH-11019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
482 | 0 | 1100 | TGD-11020 | TGD-11020 | V1105A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
483 | 0 | 1100 | TGD-11020 | TGAH-11020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
484 | 0 | 1100 | TGD-11020 | TGAHH-11020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
485 | 0 | 1100 | TGD-11021 | TGD-11021 | V-1107A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
486 | 0 | 1100 | TGD-11021 | TGAH-11021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
487 | 0 | 1100 | TGD-11021 | TGAHH-11021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
488 | 0 | 1100 | TGD-11022 | TGD-11022 | V-1107B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA74 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
489 | 0 | 1100 | TGD-11022 | TGAH-11022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
490 | 0 | 1100 | TGD-11022 | TGAHH-11022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
491 | 0 | 1100 | TGD-11023 | TGD-11023 | V-1105B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
492 | 0 | 1100 | TGD-11023 | TGAH-11023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
493 | 0 | 1100 | TGD-11023 | TGAHH-11023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
494 | 0 | 1100 | TGD-11024 | TGD-11024 | V-1106A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
495 | 0 | 1100 | TGD-11024 | TGAH-11024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
496 | 0 | 1100 | TGD-11024 | TGAHH-11024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
497 | 0 | 1100 | TGD-11025 | TGD-11025 | V-1108A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA75 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
498 | 0 | 1100 | TGD-11025 | TGAH-11025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
499 | 0 | 1100 | TGD-11025 | TGAHH-11025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
500 | 0 | 1100 | TGD-11026 | TGD-11026 | V-1108B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
501 | 0 | 1100 | TGD-11026 | TGAH-11026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
502 | 0 | 1100 | TGD-11026 | TGAHH-11026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
503 | 0 | 1100 | TGD-11027 | TGD-11027 | V-1106B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
504 | 0 | 1100 | TGD-11027 | TGAH-11027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
505 | 0 | 1100 | TGD-11027 | TGAHH-11027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
506 | 0 | 1100 | TGD-11028 | TGD-11028 | V-1111 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA76 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
507 | 0 | 1100 | TGD-11028 | TGAH-11028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
508 | 0 | 1100 | TGD-11028 | TGAHH-11028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
366 | 1 | 1100 | TGD-11029 | TGD-11029 | V-1101 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
367 | 1 | 1100 | TGD-11029 | TGAH-11029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
368 | 1 | 1100 | TGD-11029 | TGAHH-11029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
369 | 1 | 1100 | TGD-11030 | TGD-11030 | V-1102S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
370 | 1 | 1100 | TGD-11030 | TGAH-11030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
371 | 1 | 1100 | TGD-11030 | TGAHH-11030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
372 | 1 | 1100 | TGD-11031 | TGD-11031 | V-1102 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
373 | 1 | 1100 | TGD-11031 | TGAH-11031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
374 | 1 | 1100 | TGD-11031 | TGAHH-11031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
375 | 1 | 1100 | TGD-11032 | TGD-11032 | V-1103 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
376 | 1 | 1100 | TGD-11032 | TGAH-11032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
377 | 1 | 1100 | TGD-11032 | TGAHH-11032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
378 | 1 | 1100 | TGD-11033 | TGD-11033 | V-1103S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
379 | 1 | 1100 | TGD-11033 | TGAH-11033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
380 | 1 | 1100 | TGD-11033 | TGAHH-11033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
381 | 1 | 1100 | TGD-11034 | TGD-11034 | V-1104 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
382 | 1 | 1100 | TGD-11034 | TGAH-11034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
383 | 1 | 1100 | TGD-11034 | TGAHH-11034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
384 | 1 | 1100 | TGD-11035 | TGD-11035 | V-1115 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
385 | 1 | 1100 | TGD-11035 | TGAH-11035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
386 | 1 | 1100 | TGD-11035 | TGAHH-11035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
387 | 1 | 1100 | TGD-11036 | TGD-11036 | V-1116S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
388 | 1 | 1100 | TGD-11036 | TGAH-11036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
389 | 1 | 1100 | TGD-11036 | TGAHH-11036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
390 | 1 | 1100 | TGD-11037 | TGD-11037 | V-1116 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA77 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
391 | 1 | 1100 | TGD-11037 | TGAH-11037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
392 | 1 | 1100 | TGD-11037 | TGAHH-11037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
393 | 1 | 1100 | TGD-11038 | TGD-11038 | V-1105A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
394 | 1 | 1100 | TGD-11038 | TGAH-11038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
395 | 1 | 1100 | TGD-11038 | TGAHH-11038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
396 | 1 | 1100 | TGD-11039 | TGD-11039 | V-1107A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
397 | 1 | 1100 | TGD-11039 | TGAH-11039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
398 | 1 | 1100 | TGD-11039 | TGAHH-11039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
399 | 1 | 1100 | TGD-11040 | TGD-11040 | V-1107B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
400 | 1 | 1100 | TGD-11040 | TGAH-11040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
401 | 1 | 1100 | TGD-11040 | TGAHH-11040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
402 | 1 | 1100 | TGD-11041 | TGD-11041 | V-1105B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA78 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
403 | 1 | 1100 | TGD-11041 | TGAH-11041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
404 | 1 | 1100 | TGD-11041 | TGAHH-11041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
405 | 1 | 1100 | TGD-11042 | TGD-11042 | V-1106A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
406 | 1 | 1100 | TGD-11042 | TGAH-11042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
407 | 1 | 1100 | TGD-11042 | TGAHH-11042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
408 | 1 | 1100 | TGD-11043 | TGD-11043 | V-1108A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
409 | 1 | 1100 | TGD-11043 | TGAH-11043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
410 | 1 | 1100 | TGD-11043 | TGAHH-11043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
411 | 1 | 1100 | TGD-11044 | TGD-11044 | V-1108B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
412 | 1 | 1100 | TGD-11044 | TGAH-11044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
413 | 1 | 1100 | TGD-11044 | TGAHH-11044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
414 | 1 | 1100 | TGD-11045 | TGD-11045 | V-1106B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1102 | AIR | NIS | FGDS | CRR | d | F | 1100JNA79 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
415 | 1 | 1100 | TGD-11045 | TGAH-11045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
416 | 1 | 1100 | TGD-11045 | TGAHH-11045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
417 | 1 | 1100 | FD-11001 | FD-11001 | P-1101 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
418 | 1 | 1100 | FD-11001 | FAH-11001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
419 | 3 | 0000 | FD-11001 | FAH-11001B | Fire and Gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND11 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
420 | 2 | 0003 | FD-11001 | FAH-11001C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
421 | 1 | 1100 | FD-11002 | FD-11002 | P-1103 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA70 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
422 | 1 | 1100 | FD-11002 | FAH-11002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
423 | 1 | 1100 | FD-11003 | FD-11003 | P-1111 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA70 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
424 | 1 | 1100 | FD-11003 | FAH-11003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
425 | 1 | 1100 | FD-11004 | FD-11004 | P-1109 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA70 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
426 | 1 | 1100 | FD-11004 | FAH-11004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
427 | 1 | 1100 | FD-11005 | FD-11005 | P-1130 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA71 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
428 | 1 | 1100 | FD-11005 | FAH-11005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
429 | 1 | 1100 | FD-11006 | FD-11006 | P-1134 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1102 | AI | NIS | FGDS | CRR | d | F | 1100JNA71 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
430 | 1 | 1100 | FD-11006 | FAH-11006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
431 | 1 | 1200 | IRGD-12001 | IRGD/P-12001 | V-1202 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
575 | 0 | 1200 | IRGD-12001 | IRGAH-12001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
576 | 0 | 1200 | IRGD-12001 | IRGAHH-12001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
432 | 3 | 0000 | IRGD-12000 | IRGA-12000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1200 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
433 | 3 | 0003 | IRGD-12000 | IRGA-12000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1200 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
579 | 0 | 1200 | IRGD-12002 | IRGD/P-12002 | P-1216S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
580 | 0 | 1200 | IRGD-12002 | IRGAH-12002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
581 | 0 | 1200 | IRGD-12002 | IRGAHH-12002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
582 | 0 | 1200 | IRGD-12003 | IRGD/P-12003 | P-1216 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
583 | 0 | 1200 | IRGD-12003 | IRGAH-12003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
584 | 0 | 1200 | IRGD-12003 | IRGAHH-12003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
585 | 0 | 1200 | IRGD-12004 | IRGD/P-12004 | P-1215 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
586 | 0 | 1200 | IRGD-12004 | IRGAH-12004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
587 | 0 | 1200 | IRGD-12004 | IRGAHH-12004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
434 | 1 | 1200 | IRGD-12005 | IRGD/P-12005 | V-1201 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
589 | 0 | 1200 | IRGD-12005 | IRGAH-12005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
590 | 0 | 1200 | IRGD-12005 | IRGAHH-12005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
435 | 2 | 1200 | IRGD-12006 | IRGD/P-12006 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
436 | 2 | 1200 | IRGD-12006 | IRGAH-12006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
437 | 2 | 1200 | IRGD-12006 | IRGAHH-12006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
438 | 2 | 1200 | IRGD-12007 | IRGD/P-12007 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
439 | 2 | 1200 | IRGD-12007 | IRGAH-12007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
440 | 2 | 1200 | IRGD-12007 | IRGAHH-12007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
441 | 2 | 1200 | IRGD-12008 | IRGD/P-12008 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
442 | 2 | 1200 | IRGD-12008 | IRGAH-12008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
443 | 2 | 1200 | IRGD-12008 | IRGAHH-12008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
444 | 2 | 1200 | IRGD-12009 | IRGD/P-12009 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
445 | 2 | 1200 | IRGD-12009 | IRGAH-12009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
446 | 2 | 1200 | IRGD-12009 | IRGAHH-12009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
447 | 2 | 1200 | IRGD-12010 | IRGD/P-12010 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
448 | 2 | 1200 | IRGD-12010 | IRGAH-12010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
449 | 2 | 1200 | IRGD-12010 | IRGAHH-12010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
450 | 2 | 1200 | IRGD-12011 | IRGD/P-12011 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
451 | 2 | 1200 | IRGD-12011 | IRGAH-12011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
452 | 2 | 1200 | IRGD-12011 | IRGAHH-12011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
453 | 2 | 1200 | IRGD-12012 | IRGD/P-12012 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
454 | 2 | 1200 | IRGD-12012 | IRGAH-12012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
455 | 2 | 1200 | IRGD-12012 | IRGAHH-12012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
456 | 2 | 1200 | IRGD-12013 | IRGD/P-12013 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
457 | 2 | 1200 | IRGD-12013 | IRGAH-12013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
458 | 2 | 1200 | IRGD-12013 | IRGAHH-12013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
459 | 2 | 1200 | IRGD-12014 | IRGD/P-12014 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
460 | 2 | 1200 | IRGD-12014 | IRGAH-12014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
461 | 2 | 1200 | IRGD-12014 | IRGAHH-12014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
462 | 2 | 1200 | IRGD-12015 | IRGD/P-12015 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
463 | 2 | 1200 | IRGD-12015 | IRGAH-12015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
464 | 2 | 1200 | IRGD-12015 | IRGAHH-12015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
465 | 2 | 1200 | IRGD-12016 | IRGD/P-12016 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
466 | 2 | 1200 | IRGD-12016 | IRGAH-12016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
467 | 2 | 1200 | IRGD-12016 | IRGAHH-12016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
468 | 2 | 1200 | IRGD-12017 | IRGD/P-12017 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
469 | 2 | 1200 | IRGD-12017 | IRGAH-12017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
470 | 2 | 1200 | IRGD-12017 | IRGAHH-12017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
471 | 2 | 1200 | IRGD-12018 | IRGD/P-12018 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
472 | 2 | 1200 | IRGD-12018 | IRGAH-12018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
473 | 2 | 1200 | IRGD-12018 | IRGAHH-12018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
474 | 2 | 1200 | IRGD-12019 | IRGD/P-12019 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
475 | 2 | 1200 | IRGD-12019 | IRGAH-12019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
476 | 2 | 1200 | IRGD-12019 | IRGAHH-12019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
477 | 2 | 1200 | IRGD-12020 | IRGD/P-12020 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
478 | 2 | 1200 | IRGD-12020 | IRGAH-12020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
479 | 2 | 1200 | IRGD-12020 | IRGAHH-12020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
480 | 2 | 1200 | IRGD-12021 | IRGD/P-12021 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
481 | 2 | 1200 | IRGD-12021 | IRGAH-12021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
482 | 2 | 1200 | IRGD-12021 | IRGAHH-12021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
483 | 2 | 1200 | IRGD-12022 | IRGD/P-12022 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
484 | 2 | 1200 | IRGD-12022 | IRGAH-12022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
485 | 2 | 1200 | IRGD-12022 | IRGAHH-12022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
486 | 2 | 1200 | IRGD-12023 | IRGD/P-12023 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
487 | 2 | 1200 | IRGD-12023 | IRGAH-12023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
488 | 2 | 1200 | IRGD-12023 | IRGAHH-12023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
489 | 2 | 1200 | IRGD-12024 | IRGD/P-12024 | HVAC Motor fans | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA76 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
490 | 2 | 1200 | IRGD-12024 | IRGAH-12024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
491 | 2 | 1200 | IRGD-12024 | IRGAHH-12024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
492 | 2 | 1200 | IRGD-12025 | IRGD/P-12025 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA79 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
493 | 2 | 1200 | IRGD-12025 | IRGAH-12025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
494 | 2 | 1200 | IRGD-12025 | IRGAHH-12025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
495 | 2 | 1200 | IRGD-12026 | IRGD/P-12026 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA79 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
496 | 2 | 1200 | IRGD-12026 | IRGAH-12026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
497 | 2 | 1200 | IRGD-12026 | IRGAHH-12026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
498 | 4 | 1200 | IRGD-12027 | IRGD/P-12027 | TIE-IN | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
499 | 4 | 1200 | IRGD-12027 | IRGAH-12027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [16 empty] | %LFL |  | 25
500 | 4 | 1200 | IRGD-12027 | IRGAHH-12027 | (REDFLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [16 empty] | %LFL | 50
501 | 4 | 1200 | IRGD-12028 | IRGD/P-12028 | OXIDANT CONTROL VALVE | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
502 | 4 | 1200 | IRGD-12028 | IRGAH-12028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [16 empty] | %LFL |  | 25
503 | 4 | 1200 | IRGD-12028 | IRGAHH-12028 | (REDFLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [16 empty] | %LFL | 50
504 | 2 | 1200 | TGD-12001 | TGD-12001 | HVAC ROOM |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA79 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
505 | 2 | 1200 | TGD-12001 | TGAH-12001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM |  | 10
506 | 2 | 1200 | TGD-12001 | TGAHH-12001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM | 50
507 | 3 | 0000 | TGD-12000 | TGA-12000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OF AREA 1300 & 2300 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
508 | 3 | 0003 | TGD-12000 | TGA-12000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1300 & 2300 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
509 | 2 | 1200 | TGD-12002 | TGD-12002 | HVAC ROOM |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA79 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
510 | 2 | 1200 | TGD-12002 | TGAH-12002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM |  | 10
511 | 2 | 1200 | TGD-12002 | TGAHH-12002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM | 50
512 | 4 | 1200 | TGD-12003 | TGD-12003 | TIE-IN |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
513 | 4 | 1200 | TGD-12003 | TGAH-12003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM |  | 10
514 | 4 | 1200 | TGD-12003 | TGAHH-12003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-LYT-1202 | [5 empty] | OWS | [10 empty] | PPM | 50
515 | 3 | 1200 | SD-12001 | SD-12001 | HVAC ROOM | SMOKE DETECTOR | SMOKE DETECTOR | ESBR-HS-LYT-1202 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
516 | 2 | 1200 | SD-12001 | SA-12001 | ALARM
517 | 3 | 0000 | SD-12001 | SA-12001B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1200 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
518 | 2 | 1200 | SD-12001 | SA-12001C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1200 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
519 | 2 | 1200 | FD-12001 | FD-12001 | P-1215, P-1216/S |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1202 | AIR | NIS | FGDS | CRR | d | F | 1200JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
520 | 1 | 1200 | FD-12001 | FAH-12001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
521 | 3 | 0000 | FD-12000 | FAH-12000B | Fire and Gas, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1200 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
522 | 3 | 0003 | FD-12000 | FAH-12000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1200 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
523 | 3 | 6000 | HVAC-6000 | MHKL-Y6001 | Shutdown all HVAC System & Dampers Preparartion |  | FGS signal to HVAC | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
524 | 3 | 6000 | HVAC-6000 | XL-Y6000 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0006 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
525 | 3 | 6000 | HVAC-6000 | HVAC-Y6000 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0006 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
526 | 4 | 6000 | HVAC-6000 | XL-Y6001 | Operation Without Fault |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
527 | 4 | 6000 | HVAC-6000 | XL-Y6002 | Operation With Fault |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
528 | 4 | 6000 | HVAC-6000 | XL-Y6003 | Operation Stop due to Fault |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
529 | 4 | 6000 | HVAC-6000 | XL-Y6004 | MFD‐FCR‐001 status |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
530 | 4 | 6000 | HVAC-6000 | XL-Y6005 | MFD‐FCR‐002 status |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
531 | 4 | 6000 | HVAC-6000 | XL-Y6006 | MFD‐FCR‐003 status |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
532 | 4 | 6000 | HVAC-6000 | XL-Y6007 | MFD‐FCR‐004 status |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
533 | 4 | 6000 | HVAC-6000 | XL-Y6008 | FGD‐FCR‐001 status |  | HVAC signals to FGS | ESBR‐HV‐PID‐1206 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC6000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
534 | 4 | 1200 | HVAC-1200 | MHKL-Y12001 | Shutdown all HVAC System & Dampers Preparartion |  | FGS signal to HVAC | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC1200 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
535 | 4 | 1200 | HVAC-1200 | XL-Y1200 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0006 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC1200 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
536 | 4 | 1200 | HVAC-1200 | HVAC-Y1200 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0006 | DIR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC1200 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
537 | 4 | 1200 | HVAC-1200 | MHKL-Y12002 | TURN OFF MOTORIZED EXHAUST FANS (EF-CHP-001~078) |  | FGS signal to HVAC | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | HVAC-1200 | HVAC1200 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
538 | 1 | 1300 | IRGD-13001 | IRGD/P-13001 | R-1301 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
674 | 0 | 1300 | IRGD-13001 | IRGAH-13001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
675 | 0 | 1300 | IRGD-13001 | IRGAHH-13001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
539 | 3 | 0000 | IRGD-13000 | IRGA-13000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1300 & 2300 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
540 | 3 | 0003 | IRGD-13000 | IRGA-13000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1300 & 2300 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
541 | 1 | 1300 | IRGD-13002 | IRGD/P-13002 | R-1302 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
679 | 0 | 1300 | IRGD-13002 | IRGAH-13002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
680 | 0 | 1300 | IRGD-13002 | IRGAHH-13002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
542 | 1 | 1300 | IRGD-13003 | IRGD/P-13003 | R-1303 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
682 | 0 | 1300 | IRGD-13003 | IRGAH-13003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
683 | 0 | 1300 | IRGD-13003 | IRGAHH-13003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
543 | 1 | 1300 | IRGD-13004 | IRGD/P-13004 | R-1304 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
685 | 0 | 1300 | IRGD-13004 | IRGAH-13004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
686 | 0 | 1300 | IRGD-13004 | IRGAHH-13004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
544 | 1 | 1300 | IRGD-13005 | IRGD/P-13005 | R-1305 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
688 | 0 | 1300 | IRGD-13005 | IRGAH-13005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
689 | 0 | 1300 | IRGD-13005 | IRGAHH-13005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
545 | 1 | 1300 | IRGD-13006 | IRGD/P-13006 | R-1306 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
691 | 0 | 1300 | IRGD-13006 | IRGAH-13006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
692 | 0 | 1300 | IRGD-13006 | IRGAHH-13006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
546 | 1 | 1300 | IRGD-13007 | IRGD/P-13007 | R-1307 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
694 | 0 | 1300 | IRGD-13007 | IRGAH-13007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
695 | 0 | 1300 | IRGD-13007 | IRGAHH-13007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
547 | 1 | 1300 | IRGD-13008 | IRGD/P-13008 | R-1308 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
697 | 0 | 1300 | IRGD-13008 | IRGAH-13008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
698 | 0 | 1300 | IRGD-13008 | IRGAHH-13008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
548 | 1 | 1300 | IRGD-13009 | IRGD/P-13009 | R-1309 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
700 | 0 | 1300 | IRGD-13009 | IRGAH-13009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
701 | 0 | 1300 | IRGD-13009 | IRGAHH-13009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
549 | 1 | 1300 | IRGD-13010 | IRGD/P-13010 | R-1310 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
703 | 0 | 1300 | IRGD-13010 | IRGAH-13010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
704 | 0 | 1300 | IRGD-13010 | IRGAHH-13010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
550 | 1 | 1300 | IRGD-13011 | IRGD/P-13011 | R-1311 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
706 | 0 | 1300 | IRGD-13011 | IRGAH-13011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
707 | 0 | 1300 | IRGD-13011 | IRGAHH-13011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
551 | 1 | 1300 | IRGD-13012 | IRGD/P-13012 | R-1312 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
709 | 0 | 1300 | IRGD-13012 | IRGAH-13012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
710 | 0 | 1300 | IRGD-13012 | IRGAHH-13012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
552 | 1 | 1300 | IRGD-13013 | IRGD/P-13013 | R-1313 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
712 | 0 | 1300 | IRGD-13013 | IRGAH-13013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
713 | 0 | 1300 | IRGD-13013 | IRGAHH-13013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
553 | 1 | 1300 | IRGD-13014 | IRGD/P-13014 | R1314 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
715 | 0 | 1300 | IRGD-13014 | IRGAH-13014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
716 | 0 | 1300 | IRGD-13014 | IRGAHH-13014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
554 | 4 | 1300 | IRGD-13015 | IRGD/P-13015 | V-1315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
718 | 0 | 1300 | IRGD-13015 | IRGAH-13015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
719 | 0 | 1300 | IRGD-13015 | IRGAHH-13015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
555 | 1 | 1300 | IRGD-13016 | IRGD/P-13016 | E-1315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
721 | 0 | 1300 | IRGD-13016 | IRGAH-13016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
722 | 0 | 1300 | IRGD-13016 | IRGAHH-13016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
556 | 1 | 1300 | IRGD-13017 | IRGD/OPT-13017 | R-1315A~J | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 |  |  |  |  | d | F
557 | 1 | 1300 | IRGD-13017 | IRGD/OPR-13017 | R-1315A~J | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
725 | 0 | 1300 | IRGD-13017 | IRGAH-13017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
726 | 0 | 1300 | IRGD-13017 | IRGAHH-13017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
558 | 1 | 1300 | IRGD-13018 | IRGD/P-13018 | V-1317 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
728 | 0 | 1300 | IRGD-13018 | IRGAH-13018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
729 | 0 | 1300 | IRGD-13018 | IRGAHH-13018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
559 | 1 | 1300 | IRGD-13019 | IRGD/P-13019 | V-1317S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
731 | 0 | 1300 | IRGD-13019 | IRGAH-13019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
732 | 0 | 1300 | IRGD-13019 | IRGAHH-13019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
560 | 1 | 1300 | IRGD-13020 | IRGD/P-13020 | V-1319 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
734 | 0 | 1300 | IRGD-13020 | IRGAH-13020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
735 | 0 | 1300 | IRGD-13020 | IRGAHH-13020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
561 | 1 | 1300 | IRGD-13021 | IRGD/P-13021 | R-1301 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
562 | 1 | 1300 | IRGD-13021 | IRGAH-13021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
563 | 1 | 1300 | IRGD-13021 | IRGAHH-13021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
564 | 1 | 1300 | IRGD-13022 | IRGD/P-13022 | R-1302 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
565 | 1 | 1300 | IRGD-13022 | IRGAH-13022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
566 | 1 | 1300 | IRGD-13022 | IRGAHH-13022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
567 | 1 | 1300 | IRGD-13023 | IRGD/P-13023 | R-1303 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
568 | 1 | 1300 | IRGD-13023 | IRGAH-13023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
569 | 1 | 1300 | IRGD-13023 | IRGAHH-13023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
570 | 1 | 1300 | IRGD-13024 | IRGD/P-13024 | R-1304 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
571 | 1 | 1300 | IRGD-13024 | IRGAH-13024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
572 | 1 | 1300 | IRGD-13024 | IRGAHH-13024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
573 | 1 | 1300 | IRGD-13025 | IRGD/P-13025 | R-1305 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
574 | 1 | 1300 | IRGD-13025 | IRGAH-13025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
575 | 1 | 1300 | IRGD-13025 | IRGAHH-13025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
576 | 1 | 1300 | IRGD-13026 | IRGD/P-13026 | R-1306 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
577 | 1 | 1300 | IRGD-13026 | IRGAH-13026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
578 | 1 | 1300 | IRGD-13026 | IRGAHH-13026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
579 | 1 | 1300 | IRGD-13027 | IRGD/P-13027 | R-1307 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
580 | 1 | 1300 | IRGD-13027 | IRGAH-13027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
581 | 1 | 1300 | IRGD-13027 | IRGAHH-13027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
582 | 1 | 1300 | IRGD-13028 | IRGD/P-13028 | R-1308 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
583 | 1 | 1300 | IRGD-13028 | IRGAH-13028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
584 | 1 | 1300 | IRGD-13028 | IRGAHH-13028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
585 | 1 | 1300 | IRGD-13029 | IRGD/P-13029 | R-1309 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
586 | 1 | 1300 | IRGD-13029 | IRGAH-13029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
587 | 1 | 1300 | IRGD-13029 | IRGAHH-13029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
588 | 4 | 1300 | IRGD-13032 | IRGD/P-13032 | V-1908 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
764 | 0 | 1300 | IRGD-13032 | IRGAH-13032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
765 | 0 | 1300 | IRGD-13032 | IRGAHH-13032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
589 | 1 | 1300 | IRGD-13033 | IRGD/OPT-13033 | V-1905 | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 |  |  |  |  | d | F
590 | 2 | 1300 | IRGD-13033 | IRGD/OPR-13033 | V-1905 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
768 | 0 | 1300 | IRGD-13033 | IRGAH-13033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
769 | 0 | 1300 | IRGD-13033 | IRGAHH-13033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
591 | 1 | 1300 | IRGD-13030 | IRGD/P-13030 | V-1318 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
771 | 0 | 1300 | IRGD-13030 | IRGAH-13030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
772 | 0 | 1300 | IRGD-13030 | IRGAHH-13030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
592 | 1 | 1300 | IRGD-13031 | IRGD/P-13031 | V-1320 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
774 | 0 | 1300 | IRGD-13031 | IRGAH-13031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
775 | 0 | 1300 | IRGD-13031 | IRGAHH-13031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
593 | 1 | 1300 | IRGD-13034 | IRGD/P-13034 | V-1325 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
777 | 0 | 1300 | IRGD-13034 | IRGAH-13034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
778 | 0 | 1300 | IRGD-13034 | IRGAHH-13034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
594 | 1 | 1300 | IRGD-13035 | IRGD/P-13035 | R-1310 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
595 | 1 | 1300 | IRGD-13035 | IRGAH-13035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
596 | 1 | 1300 | IRGD-13035 | IRGAHH-13035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
597 | 1 | 1300 | IRGD-13036 | IRGD/P-13036 | R-1311 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
598 | 1 | 1300 | IRGD-13036 | IRGAH-13036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
599 | 1 | 1300 | IRGD-13036 | IRGAHH-13036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
600 | 1 | 1300 | IRGD-13037 | IRGD/P-13037 | R-1312 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
601 | 1 | 1300 | IRGD-13037 | IRGAH-13037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
602 | 1 | 1300 | IRGD-13037 | IRGAHH-13037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
603 | 1 | 1300 | IRGD-13038 | IRGD/P-13038 | R-1313 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
604 | 1 | 1300 | IRGD-13038 | IRGAH-13038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
605 | 1 | 1300 | IRGD-13038 | IRGAHH-13038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
606 | 1 | 1300 | IRGD-13039 | IRGD/P-13039 | R-1314 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
607 | 1 | 1300 | IRGD-13039 | IRGAH-13039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
608 | 1 | 1300 | IRGD-13039 | IRGAHH-13039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
609 | 1 | 1300 | IRGD-13040 | IRGD/P-13040 | V-1317 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
610 | 1 | 1300 | IRGD-13040 | IRGAH-13040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
611 | 1 | 1300 | IRGD-13040 | IRGAHH-13040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
612 | 1 | 1300 | IRGD-13041 | IRGD/P-13041 | V-1317S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
613 | 1 | 1300 | IRGD-13041 | IRGAH-13041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
614 | 1 | 1300 | IRGD-13041 | IRGAHH-13041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
615 | 1 | 1300 | IRGD-13042 | IRGD/P-13042 | V-1319 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
616 | 1 | 1300 | IRGD-13042 | IRGAH-13042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
617 | 1 | 1300 | IRGD-13042 | IRGAHH-13042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
618 | 4 | 1300 | IRGD-13043 | IRGD/P-13043 | V-1315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
619 | 1 | 1300 | IRGD-13043 | IRGAH-13043 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
620 | 1 | 1300 | IRGD-13043 | IRGAHH-13043 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
621 | 1 | 1300 | IRGD-13044 | IRGD/OPT-13044 | R-1315A~J | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 |  |  |  |  | d | F
622 | 1 | 1300 | IRGD-13044 | IRGD/OPR-13044 | R-1315A~J | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
623 | 1 | 1300 | IRGD-13044 | IRGAH-13044 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
624 | 1 | 1300 | IRGD-13044 | IRGAHH-13044 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
625 | 4 | 1300 | IRGD-13045 | IRGD/P-13045 | P-1905 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 15 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
626 | 4 | 1300 | IRGD-13045 | IRGAH-13045 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
627 | 4 | 1300 | IRGD-13045 | IRGAHH-13045 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
810 | 0 | 1300 | TGD-13046 | TGD-13046 | V-1318 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
811 | 0 | 1300 | TGD-13046 | TGAH-13046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
812 | 0 | 1300 | TGD-13046 | TGAHH-13046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
813 | 0 | 1300 | TGD-13047 | TGD-13047 | V-1320 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
814 | 0 | 1300 | TGD-13047 | TGAH-13047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
815 | 0 | 1300 | TGD-13047 | TGAHH-13047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
816 | 0 | 1300 | TGD-13048 | TGD-13048 | V-1325 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 (rev.0) |  |  | FGDS | CRR | d | F | 1300JNA79 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | SYS/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
817 | 0 | 1300 | TGD-13048 | TGAH-13048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
818 | 0 | 1300 | TGD-13048 | TGAHH-13048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
819 | 0 | 1300 | TGD-13001 | TGD-13001 | R-1301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
820 | 0 | 1300 | TGD-13001 | TGAH-13001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
821 | 0 | 1300 | TGD-13001 | TGAHH-13001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
628 | 3 | 0000 | TGD-13000 | TGA-13000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OF AREA 1300 & 2300 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
629 | 3 | 0003 | TGD-13000 | TGA13000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1300 & 2300 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
824 | 0 | 1300 | TGD-13002 | TGD-13002 | R-1302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
825 | 0 | 1300 | TGD-13002 | TGAH-13002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
826 | 0 | 1300 | TGD-13002 | TGAHH-13002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
827 | 0 | 1300 | TGD-13003 | TGD-13003 | R-1303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
828 | 0 | 1300 | TGD-13003 | TGAH-13003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
829 | 0 | 1300 | TGD-13003 | TGAHH-13003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
830 | 0 | 1300 | TGD-13004 | TGD-13004 | R-1304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
831 | 0 | 1300 | TGD-13004 | TGAH-13004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
832 | 0 | 1300 | TGD-13004 | TGAHH-13004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
833 | 0 | 1300 | TGD-13005 | TGD-13005 | R-1305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
834 | 0 | 1300 | TGD-13005 | TGAH-13005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
835 | 0 | 1300 | TGD-13005 | TGAHH-13005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
836 | 0 | 1300 | TGD-13006 | TGD-13006 | R-1306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
837 | 0 | 1300 | TGD-13006 | TGAH-13006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
838 | 0 | 1300 | TGD-13006 | TGAHH-13006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
839 | 0 | 1300 | TGD-13007 | TGD-13007 | R-1307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
840 | 0 | 1300 | TGD-13007 | TGAH-13007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
841 | 0 | 1300 | TGD-13007 | TGAHH-13007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
842 | 0 | 1300 | TGD-13008 | TGD-13008 | R1308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
843 | 0 | 1300 | TGD-13008 | TGAH-13008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
844 | 0 | 1300 | TGD-13008 | TGAHH-13008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
845 | 0 | 1300 | TGD-13009 | TGD-13009 | R-1309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
846 | 0 | 1300 | TGD-13009 | TGAH-13009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
847 | 0 | 1300 | TGD-13009 | TGAHH-13009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
848 | 0 | 1300 | TGD-13010 | TGD-13010 | R-1310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
849 | 0 | 1300 | TGD-13010 | TGAH-13010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
850 | 0 | 1300 | TGD-13010 | TGAHH-13010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
851 | 0 | 1300 | TGD-13011 | TGD-13011 | R-1311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
852 | 0 | 1300 | TGD-13011 | TGAH-13011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
853 | 0 | 1300 | TGD-13011 | TGAHH-13011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
854 | 0 | 1300 | TGD-13012 | TGD-13012 | R-1312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
855 | 0 | 1300 | TGD-13012 | TGAH-13012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
856 | 0 | 1300 | TGD-13012 | TGAHH-13012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
857 | 0 | 1300 | TGD-13013 | TGD-13013 | R-1313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
858 | 0 | 1300 | TGD-13013 | TGAH-13013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
859 | 0 | 1300 | TGD-13013 | TGAHH-13013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
860 | 0 | 1300 | TGD-13014 | TGD-13014 | R-1314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA73 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
861 | 0 | 1300 | TGD-13014 | TGAH-13014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
862 | 0 | 1300 | TGD-13014 | TGAHH-13014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
630 | 4 | 1300 | TGD-13015 | TGD-13015 | V-1315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
864 | 0 | 1300 | TGD-13015 | TGAH-13015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
865 | 0 | 1300 | TGD-13015 | TGAHH-13015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
866 | 0 | 1300 | TGD-13016 | TGD-13016 | E-1315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
867 | 0 | 1300 | TGD-13016 | TGAH-13016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
868 | 0 | 1300 | TGD-13016 | TGAHH-13016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
869 | 0 | 1300 | TGD-13017 | TGD-13017 | V-1316 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
870 | 0 | 1300 | TGD-13017 | TGAH-13017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
871 | 0 | 1300 | TGD-13017 | TGAHH-13017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
631 | 1 | 1300 | TGD-13018 | TGD-13018 | V-1301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
873 | 0 | 1300 | TGD-13018 | TGAH-13018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
874 | 0 | 1300 | TGD-13018 | TGAHH-13018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
632 | 1 | 1300 | TGD-13019 | TGD-13019 | V-1302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
876 | 0 | 1300 | TGD-13019 | TGAH-13019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
877 | 0 | 1300 | TGD-13019 | TGAHH-13019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
633 | 1 | 1300 | TGD-13020 | TGD-13020 | V-1303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
879 | 0 | 1300 | TGD-13020 | TGAH-13020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
880 | 0 | 1300 | TGD-13020 | TGAHH-13020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
634 | 1 | 1300 | TGD-13021 | TGD-13021 | V-1304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
882 | 0 | 1300 | TGD-13021 | TGAH-13021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
883 | 0 | 1300 | TGD-13021 | TGAHH-13021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
635 | 1 | 1300 | TGD-13022 | TGD-13022 | V-1305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
885 | 0 | 1300 | TGD-13022 | TGAH-13022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
886 | 0 | 1300 | TGD-13022 | TGAHH-13022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
636 | 1 | 1300 | TGD-13023 | TGD-13023 | V-1306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
888 | 0 | 1300 | TGD-13023 | TGAH-13023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
889 | 0 | 1300 | TGD-13023 | TGAHH-13023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
637 | 1 | 1300 | TGD-13024 | TGD-13024 | V-1307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
891 | 0 | 1300 | TGD-13024 | TGAH-13024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
892 | 0 | 1300 | TGD-13024 | TGAHH-13024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
638 | 1 | 1300 | TGD-13025 | TGD-13025 | V-1308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
894 | 0 | 1300 | TGD-13025 | TGAH-13025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
895 | 0 | 1300 | TGD-13025 | TGAHH-13025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
639 | 1 | 1300 | TGD-13026 | TGD-13026 | V-1309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
897 | 0 | 1300 | TGD-13026 | TGAH-13026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
898 | 0 | 1300 | TGD-13026 | TGAHH-13026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
640 | 1 | 1300 | TGD-13027 | TGD-13027 | V-1310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
900 | 0 | 1300 | TGD-13027 | TGAH-13027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
901 | 0 | 1300 | TGD-13027 | TGAHH-13027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
641 | 1 | 1300 | TGD-13028 | TGD-13028 | V-1311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
903 | 0 | 1300 | TGD-13028 | TGAH-13028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
904 | 0 | 1300 | TGD-13028 | TGAHH-13028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
642 | 1 | 1300 | TGD-13029 | TGD-13029 | V-1312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
906 | 0 | 1300 | TGD-13029 | TGAH-13029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
907 | 0 | 1300 | TGD-13029 | TGAHH-13029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
643 | 1 | 1300 | TGD-13030 | TGD-13030 | V-1313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
909 | 0 | 1300 | TGD-13030 | TGAH-13030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
910 | 0 | 1300 | TGD-13030 | TGAHH-13030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
644 | 1 | 1300 | TGD-13031 | TGD-13031 | V-1314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
912 | 0 | 1300 | TGD-13031 | TGAH-13031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
913 | 0 | 1300 | TGD-13031 | TGAHH-13031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
645 | 1 | 1300 | TGD-13032 | TGD-13032 | R-1315A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
915 | 0 | 1300 | TGD-13032 | TGAH-13032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
916 | 0 | 1300 | TGD-13032 | TGAHH-13032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
646 | 1 | 1300 | TGD-13033 | TGD-13033 | R-1315C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
918 | 0 | 1300 | TGD-13033 | TGAH-13033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
919 | 0 | 1300 | TGD-13033 | TGAHH-13033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
647 | 1 | 1300 | TGD-13034 | TGD-13034 | R-1315E |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
921 | 0 | 1300 | TGD-13034 | TGAH-13034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
922 | 0 | 1300 | TGD-13034 | TGAHH-13034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
648 | 1 | 1300 | TGD-13035 | TGD-13035 | R-1315G |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
924 | 0 | 1300 | TGD-13035 | TGAH-13035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
925 | 0 | 1300 | TGD-13035 | TGAHH-13035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
649 | 1 | 1300 | TGD-13036 | TGD-13036 | R-1315I |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
927 | 0 | 1300 | TGD-13036 | TGAH-13036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
928 | 0 | 1300 | TGD-13036 | TGAHH-13036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
650 | 4 | 1300 | TGD-13037 | TGD-13037 | V-1908 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
651 | 1 | 1300 | TGD-13037 | TGAH-13037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
652 | 1 | 1300 | TGD-13037 | TGAHH-13037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
653 | 1 | 1300 | TGD-13038 | TGD-13038 | E-1315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
654 | 1 | 1300 | TGD-13038 | TGAH-13038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
655 | 1 | 1300 | TGD-13038 | TGAHH-13038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
656 | 1 | 1300 | TGD-13039 | TGD-13039 | V-1319 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
657 | 1 | 1300 | TGD-13039 | TGAH-13039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
658 | 1 | 1300 | TGD-13039 | TGAHH-13039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
659 | 1 | 1300 | TGD-13040 | TGD-13040 | V-1317 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
660 | 1 | 1300 | TGD-13040 | TGAH-13040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
661 | 1 | 1300 | TGD-13040 | TGAHH-13040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
662 | 1 | 1300 | TGD-13041 | TGD-13041 | V-1317S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
663 | 1 | 1300 | TGD-13041 | TGAH-13041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
664 | 1 | 1300 | TGD-13041 | TGAHH-13041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
665 | 1 | 1300 | TGD-13042 | TGD-13042 | V-1317 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
945 | 0 | 1300 | TGD-13042 | TGAH-13042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
946 | 0 | 1300 | TGD-13042 | TGAHH-13042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
666 | 1 | 1300 | TGD-13043 | TGD-13043 | V-1317S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
948 | 0 | 1300 | TGD-13043 | TGAH-13043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
949 | 0 | 1300 | TGD-13043 | TGAHH-13043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
667 | 1 | 1300 | TGD-13044 | TGD-13044 | V-1319 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA78 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
951 | 0 | 1300 | TGD-13044 | TGAH-13044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
952 | 0 | 1300 | TGD-13044 | TGAHH-13044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
953 | 0 | 1300 | TGD-13045 | TGD-13045 | V-1323 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
954 | 0 | 1300 | TGD-13045 | TGAH-13045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
955 | 0 | 1300 | TGD-13045 | TGAHH-13045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
668 | 4 | 1300 | TGD-13048 | TGD-13048 | V-1316 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
669 | 1 | 1300 | TGD-13048 | TGAH-13048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
670 | 1 | 1300 | TGD-13048 | TGAHH-13048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
671 | 4 | 1300 | TGD-13049 | TGD-13049 | V-1315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA88 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
672 | 1 | 1300 | TGD-13049 | TGAH-13049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
673 | 1 | 1300 | TGD-13049 | TGAHH-13049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
674 | 1 | 1300 | TGD-13050 | TGD-13050 | R-1301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
675 | 1 | 1300 | TGD-13050 | TGAH-13050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
676 | 1 | 1300 | TGD-13050 | TGAHH-13050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
677 | 1 | 1300 | TGD-13051 | TGD-13051 | R-1302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
678 | 1 | 1300 | TGD-13051 | TGAH-13051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
679 | 1 | 1300 | TGD-13051 | TGAHH-13051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
680 | 1 | 1300 | TGD-13052 | TGD-13052 | R-1303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
681 | 1 | 1300 | TGD-13052 | TGAH-13052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
682 | 1 | 1300 | TGD-13052 | TGAHH-13052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
683 | 1 | 1300 | TGD-13053 | TGD-13053 | R-1304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
684 | 1 | 1300 | TGD-13053 | TGAH-13053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
685 | 1 | 1300 | TGD-13053 | TGAHH-13053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
686 | 1 | 1300 | TGD-13054 | TGD-13054 | R-1305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
687 | 1 | 1300 | TGD-13054 | TGAH-13054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
688 | 1 | 1300 | TGD-13054 | TGAHH-13054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
689 | 1 | 1300 | TGD-13055 | TGD-13055 | R-1306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
690 | 1 | 1300 | TGD-13055 | TGAH-13055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
691 | 1 | 1300 | TGD-13055 | TGAHH-13055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
692 | 1 | 1300 | TGD-13056 | TGD-13056 | R-1307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
693 | 1 | 1300 | TGD-13056 | TGAH-13056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
694 | 1 | 1300 | TGD-13056 | TGAHH-13056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
695 | 1 | 1300 | TGD-13057 | TGD-13057 | R-1308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
696 | 1 | 1300 | TGD-13057 | TGAH-13057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
697 | 1 | 1300 | TGD-13057 | TGAHH-13057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
698 | 1 | 1300 | TGD-13058 | TGD-13058 | R-1309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
699 | 1 | 1300 | TGD-13058 | TGAH-13058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
700 | 1 | 1300 | TGD-13058 | TGAHH-13058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
701 | 1 | 1300 | TGD-13059 | TGD-13059 | R-1310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA76 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
702 | 1 | 1300 | TGD-13059 | TGAH-13059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
703 | 1 | 1300 | TGD-13059 | TGAHH-13059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
704 | 1 | 1300 | TGD-13060 | TGD-13060 | R-1311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
705 | 1 | 1300 | TGD-13060 | TGAH-13060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
706 | 1 | 1300 | TGD-13060 | TGAHH-13060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
707 | 1 | 1300 | TGD-13061 | TGD-13061 | R-1312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
708 | 1 | 1300 | TGD-13061 | TGAH-13061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
709 | 1 | 1300 | TGD-13061 | TGAHH-13061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
710 | 1 | 1300 | TGD-13062 | TGD-13062 | R-1313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
711 | 1 | 1300 | TGD-13062 | TGAH-13062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
712 | 1 | 1300 | TGD-13062 | TGAHH-13062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
713 | 1 | 1300 | TGD-13063 | TGD-13063 | R-1314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA77 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
714 | 1 | 1300 | TGD-13063 | TGAH-13063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
715 | 1 | 1300 | TGD-13063 | TGAHH-13063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
716 | 1 | 1300 | TGD-13064 | TGD-13064 | R-1315A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
717 | 1 | 1300 | TGD-13064 | TGAH-13064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
718 | 1 | 1300 | TGD-13064 | TGAHH-13064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
719 | 1 | 1300 | TGD-13065 | TGD-13065 | R-1315C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
720 | 1 | 1300 | TGD-13065 | TGAH-13065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
721 | 1 | 1300 | TGD-13065 | TGAHH-13065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
722 | 1 | 1300 | TGD-13066 | TGD-13066 | R-1315E |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
723 | 1 | 1300 | TGD-13066 | TGAH-13066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
724 | 1 | 1300 | TGD-13066 | TGAHH-13066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
725 | 1 | 1300 | TGD-13067 | TGD-13067 | R-1315G |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
726 | 1 | 1300 | TGD-13067 | TGAH-13067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
727 | 1 | 1300 | TGD-13067 | TGAHH-13067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
728 | 1 | 1300 | TGD-13068 | TGD-13068 | R-1315I |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA80 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
729 | 1 | 1300 | TGD-13068 | TGAH-13068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
730 | 1 | 1300 | TGD-13068 | TGAHH-13068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
731 | 4 | 1300 | TGD-13069 | TGD-13069 | R-1313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
732 | 4 | 1300 | TGD-13069 | TGAH-13069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
733 | 4 | 1300 | TGD-13069 | TGAHH-13069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
734 | 4 | 1300 | TGD-13070 | TGD-13070 | R-1301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
735 | 4 | 1300 | TGD-13070 | TGAH-13070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
736 | 4 | 1300 | TGD-13070 | TGAHH-13070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
737 | 4 | 1300 | TGD-13071 | TGD-13071 | R-1302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA74 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
738 | 4 | 1300 | TGD-13071 | TGAH-13071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
739 | 4 | 1300 | TGD-13071 | TGAHH-13071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
740 | 4 | 1300 | TGD-13072 | TGD-13072 | R-1303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
741 | 4 | 1300 | TGD-13072 | TGAH-13072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
742 | 4 | 1300 | TGD-13072 | TGAHH-13072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
743 | 4 | 1300 | TGD-13073 | TGD-13073 | R-1304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA75 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
744 | 4 | 1300 | TGD-13073 | TGAH-13073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
745 | 4 | 1300 | TGD-13073 | TGAHH-13073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
746 | 4 | 1300 | TGD-13074 | TGD-13074 | R-1305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
747 | 4 | 1300 | TGD-13074 | TGAH-13074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
748 | 4 | 1300 | TGD-13074 | TGAHH-13074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
749 | 4 | 1300 | TGD-13075 | TGD-13075 | R-1306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
750 | 4 | 1300 | TGD-13075 | TGAH-13075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
751 | 4 | 1300 | TGD-13075 | TGAHH-13075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
752 | 4 | 1300 | TGD-13076 | TGD-13076 | R-1307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
753 | 4 | 1300 | TGD-13076 | TGAH-13076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
754 | 4 | 1300 | TGD-13076 | TGAHH-13076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
755 | 4 | 1300 | TGD-13077 | TGD-13077 | R-1308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
756 | 4 | 1300 | TGD-13077 | TGAH-13077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
757 | 4 | 1300 | TGD-13077 | TGAHH-13077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
758 | 4 | 1300 | TGD-13078 | TGD-13078 | R-1309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
759 | 4 | 1300 | TGD-13078 | TGAH-13078 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
760 | 4 | 1300 | TGD-13078 | TGAHH-13078 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
761 | 4 | 1300 | TGD-13079 | TGD-13079 | R-1310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
762 | 4 | 1300 | TGD-13079 | TGAH-13079 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
763 | 4 | 1300 | TGD-13079 | TGAHH-13079 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
764 | 4 | 1300 | TGD-13080 | TGD-13080 | R-1311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
765 | 4 | 1300 | TGD-13080 | TGAH-13080 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
766 | 4 | 1300 | TGD-13080 | TGAHH-13080 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
767 | 4 | 1300 | TGD-13081 | TGD-13081 | R-1312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
768 | 4 | 1300 | TGD-13081 | TGAH-13081 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
769 | 4 | 1300 | TGD-13081 | TGAHH-13081 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
770 | 4 | 1300 | TGD-13082 | TGD-13082 | R-1313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
771 | 4 | 1300 | TGD-13082 | TGAH-13082 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
772 | 4 | 1300 | TGD-13082 | TGAHH-13082 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
773 | 4 | 1300 | TGD-13083 | TGD-13083 | R-1314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA89 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
774 | 4 | 1300 | TGD-13083 | TGAH-13083 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
775 | 4 | 1300 | TGD-13083 | TGAHH-13083 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
776 | 2 | 1300 | FD-13001 | FD-13001 | P-1905 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA70 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
777 | 1 | 1300 | FD-13001 | FAH-13001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
778 | 3 | 0000 | FD-13000 | FAH-13000B | Fire and Gas, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1300 & 2300 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
779 | 3 | 0003 | FD-13000 | FAH-13000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1300 & 2300 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
780 | 4 | 1300 | FD-13002 | FD-13002 | K-1301 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA72 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
781 | 4 | 1300 | FD-13002 | FAH-13002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
782 | 4 | 1300 | FD-13003 | FD-13003 | V-1325 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1302 | AIR | NIS | FGDS | CRR | d | F | 1300JNA79 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
783 | 4 | 1300 | FD-13003 | FAH-13003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1023 | 0 | 1700 | TGD-17001 | TGD-17001 | V-1701 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1702 | AIR | NIS | FGDS | CRR | d | F | 1700JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1024 | 0 | 1700 | TGD-17001 | TGAH-17001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1025 | 0 | 1700 | TGD-17001 | TGAHH-17001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
784 | 3 | 0000 | TGD-17000 | TGA-17000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 1700 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
785 | 3 | 0003 | TGD-17000 | TGA17000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1700 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
786 | 1 | 1700 | TGD-1700X | TGD-1700X | Y-1750 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1702 | AIR | NIS | FGDS | CRR | d | F | 1700JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
787 | 1 | 1700 | TGD-1700X | TGAH-1700X | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
788 | 1 | 1700 | TGD-1700X | TGAHH-1700X | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
789 | 2 | 1700 | FD-1700X | FD-1700X |  |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1702 | AIR | NIS | FGDS | CRR | d | F | 1700JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
790 | 1 | 1700 | FD-1700X | FAH-1700X | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
791 | 3 | 0000 | FD-1700X | FAH-1700XB | Fire and Gas, Signal to CCR | FLAME DETECTOR STATUS LAMP OF AREA 1700 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
792 | 1 | 0003 | FD-1700X | FA1700XC | Signal connection through remote I/O | FLAME DETECTOR STATUS LAMP OF AREA 1700 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
793 | 1 | 1800 | TGD-18001 | TGD-18001 | V-1808B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
794 | 1 | 1800 | TGD-18001 | TGAH-18001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
795 | 1 | 1800 | TGD-18001 | TGAHH-18001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
796 | 1 | 1800 | TGD-18002 | TGD-18002 | V-1808A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
797 | 1 | 1800 | TGD-18002 | TGAH-18002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
798 | 1 | 1800 | TGD-18002 | TGAHH-18002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
799 | 1 | 1800 | TGD-18003 | TGD-18003 | P-1802 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1042 | 0 | 1800 | TGD-18003 | TGAH-18003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1043 | 0 | 1800 | TGD-18003 | TGAHH-18003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
800 | 1 | 1800 | TGD-18004 | TGD-18004 | V-1801B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1045 | 0 | 1800 | TGD-18004 | TGAH-18004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1046 | 0 | 1800 | TGD-18004 | TGAHH-18004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
801 | 1 | 1800 | TGD-18005 | TGD-18005 | V-1801A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1048 | 0 | 1800 | TGD-18005 | TGAH-18005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1049 | 0 | 1800 | TGD-18005 | TGAHH-18005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
802 | 1 | 1800 | TGD-18006 | TGD-18006 | E-1801 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1051 | 0 | 1800 | TGD-18006 | TGAH-18006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1052 | 0 | 1800 | TGD-18006 | TGAHH-18006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
803 | 1 | 1800 | TGD-18007 | TGD-18007 | E-1901 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1054 | 0 | 1800 | TGD-18007 | TGAH-18007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1055 | 0 | 1800 | TGD-18007 | TGAHH-18007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
804 | 1 | 1800 | TGD-18008 | TGD-18008 | V-1901 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
805 | 1 | 1800 | TGD-18008 | TGAH-18008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
806 | 1 | 1800 | TGD-18008 | TGAHH-18008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
807 | 1 | 1800 | IRGD-18017 | IRGD/P-18017 | S-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
808 | 1 | 1800 | TGD-18009 | TGAH-18009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
809 | 1 | 1800 | TGD-18009 | TGAHH-18009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
810 | 1 | 1800 | TGD-18010 | TGD-18010 | V-1903 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
811 | 1 | 1800 | TGD-18010 | TGAH-18010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
812 | 1 | 1800 | TGD-18010 | TGAHH-18010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
813 | 1 | 1800 | FD-18009 | FD-18009 | P-1904 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA72 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
814 | 1 | 1800 | TGD-18011 | TGAH-18011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
815 | 1 | 1800 | TGD-18011 | TGAHH-18011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
816 | 1 | 1800 | IRGD-18011 | IRGD/P18011 | P-1903 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
817 | 1 | 1800 | TGD-18012 | TGAH-18012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
818 | 1 | 1800 | TGD-18012 | TGAHH-18012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
819 | 1 | 1800 | TGD-18013 | TGD-18013 | P-1902 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
820 | 1 | 1800 | TGD-18013 | TGAH-18013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
821 | 1 | 1800 | TGD-18013 | TGAHH-18013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
822 | 1 | 1800 | TGD-18014 | TGD-18014 | P-1901 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
823 | 1 | 1800 | TGD-18014 | TGAH-18014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
824 | 1 | 1800 | TGD-18014 | TGAHH-18014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
825 | 1 | 1800 | TGD-18015 | TGD-18015 | P-1806 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
826 | 1 | 1800 | TGD-18015 | TGAH-18015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
827 | 1 | 1800 | TGD-18015 | TGAHH-18015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
828 | 1 | 1800 | TGD-18016 | TGD-18016 | V-1904 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
829 | 1 | 1800 | TGD-18016 | TGAH-18016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
830 | 1 | 1800 | TGD-18016 | TGAHH-18016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
831 | 1 | 1800 | TGD-18017 | TGD-18017 | V-1806 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
832 | 1 | 1800 | TGD-18017 | TGAH-18017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
833 | 1 | 1800 | TGD-18017 | TGAHH-18017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
834 | 1 | 1800 | TGD-18018 | TGD-18018 | C-1902 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
835 | 1 | 1800 | TGD-18018 | TGAH-18018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
836 | 1 | 1800 | TGD-18018 | TGAHH-18018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
837 | 1 | 1800 | TGD-18019 | TGD-18019 | C-1901 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
838 | 1 | 1800 | TGD-18019 | TGAH-18019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
839 | 1 | 1800 | TGD-18019 | TGAHH-18019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
840 | 1 | 1800 | TGD-18020 | TGD-18020 | V-1803 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
841 | 1 | 1800 | TGD-18020 | TGAH-18020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
842 | 1 | 1800 | TGD-18020 | TGAHH-18020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
843 | 1 | 1800 | TGD-18021 | TGD-18021 | E1802 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
844 | 1 | 1800 | TGD-18021 | TGAH-18021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
845 | 1 | 1800 | TGD-18021 | TGAHH-18021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
846 | 2 | 1800 | TGD-18022 | TGD-18022 | E-1802 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
847 | 2 | 1800 | TGD-18022 | TGAH-18022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
848 | 2 | 1800 | TGD-18022 | TGAHH-18022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
849 | 1 | 1800 | TGD-18024 | TGD-18024 | C-1901 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
850 | 1 | 1800 | TGD-18024 | TGAH-18024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
851 | 1 | 1800 | TGD-18024 | TGAHH-18024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
852 | 2 | 1800 | TGD-18026 | TGD-18026 | C-1902 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
853 | 1 | 1800 | TGD-18026 | TGAH-18026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
854 | 1 | 1800 | TGD-18026 | TGAHH-18026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
855 | 1 | 1800 | TGD-18023 | TGD-18023 | V-1902 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
856 | 1 | 1800 | TGD-18023 | TGAH-18023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
857 | 1 | 1800 | TGD-18023 | TGAHH-18023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
858 | 1 | 1800 | TGD-18025 | TGD-18025 | V-1803 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
859 | 1 | 1800 | TGD-18025 | TGAH-18025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
860 | 1 | 1800 | TGD-18025 | TGAHH-18025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
861 | 1 | 1800 | IRGD-18001 | IRGD/P-18001 | P-1814 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1114 | 0 | 1800 | IRGD-18001 | IRGAH-18001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1115 | 0 | 1800 | IRGD-18001 | IRGAHH-18001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
862 | 1 | 1800 | IRGD-18002 | IRGD/P-18002 | P-1801 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1117 | 0 | 1800 | IRGD-18002 | IRGAH-18002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1118 | 0 | 1800 | IRGD-18002 | IRGAHH-18002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
863 | 1 | 1800 | IRGD-18003 | IRGD/P-18003 | V-1802 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1120 | 0 | 1800 | IRGD-18003 | IRGAH-18003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1121 | 0 | 1800 | IRGD-18003 | IRGAHH-18003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
864 | 1 | 1800 | IRGD-18004 | IRGD/P-18004 | V-1801B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1123 | 0 | 1800 | IRGD-18004 | IRGAH-18004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1124 | 0 | 1800 | IRGD-18004 | IRGAHH-18004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
865 | 1 | 1800 | IRGD-18005 | IRGD/P-18005 | V-1801A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1126 | 0 | 1800 | IRGD-18005 | IRGAH-18005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1127 | 0 | 1800 | IRGD-18005 | IRGAHH-18005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
866 | 1 | 1800 | IRGD-18006 | IRGD/P-18006 | E-1801 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1129 | 0 | 1800 | IRGD-18006 | IRGAH-18006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1130 | 0 | 1800 | IRGD-18006 | IRGAHH-18006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
867 | 1 | 1800 | IRGD-18007 | IRGD/P-18007 | P-1802 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1132 | 0 | 1800 | IRGD-18007 | IRGAH-18007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1133 | 0 | 1800 | IRGD-18007 | IRGAHH-18007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
868 | 1 | 1800 | IRGD-18008 | IRGD/OPT-18008 | V-1801A/B | Open Path Type Gas DetectorTransmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 |  |  |  |  | d | F
869 | 1 | 1800 | IRGD-18008 | IRGD/OPR-18008 | V-1801A/B | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA70 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
870 | 1 | 1800 | IRGD-18008 | IRGAH-18008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
871 | 1 | 1800 | IRGD-18008 | IRGAHH-18008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
872 | 1 | 1800 | IRGD-18009 | IRGD/P-18009 | V-1808A | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
873 | 1 | 1800 | IRGD-18009 | IRGAH-18009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
874 | 1 | 1800 | IRGD-18009 | IRGAHH-18009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
875 | 1 | 1800 | IRGD-18010 | IRGD/P-18010 | V-1808B | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
876 | 1 | 1800 | IRGD-18010 | IRGAH-18010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
877 | 1 | 1800 | IRGD-18010 | IRGAHH-18010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
878 | 1 | 1800 | TGD-18011 | TGD-18011 | P-1903 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
879 | 1 | 1800 | IRGD-18011 | IRGAH-18011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
880 | 1 | 1800 | IRGD-18011 | IRGAHH-18011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
881 | 1 | 1800 | TGD-18009 | TGD-18009 | S-1902 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
882 | 1 | 1800 | IRGD-18012 | IRGAH-18012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
883 | 1 | 1800 | IRGD-18012 | IRGAHH-18012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
884 | 1 | 1800 | IRGD-18013 | IRGD/P-18013 | P-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
885 | 1 | 1800 | IRGD-18013 | IRGAH-18013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
886 | 1 | 1800 | IRGD-18013 | IRGAHH-18013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
887 | 1 | 1800 | IRGD-18014 | IRGD/P-18014 | P-1901 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
888 | 1 | 1800 | IRGD-18014 | IRGAH-18014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
889 | 1 | 1800 | IRGD-18014 | IRGAHH-18014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
890 | 1 | 1800 | IRGD-18015 | IRGD/P-18015 | P-1806 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
891 | 1 | 1800 | IRGD-18015 | IRGAH-18015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
892 | 1 | 1800 | IRGD-18015 | IRGAHH-18015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
893 | 1 | 1800 | IRGD-18016 | IRGD/OPT-18016 | V-1901 | Open Path Type Gas DetectorTransmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 |  |  |  |  | d | F
894 | 1 | 1800 | IRGD-18016 | IRGD/OPR-18016 | V-1901 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA73 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
895 | 1 | 1800 | IRGD-18016 | IRGAH-18016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
896 | 1 | 1800 | IRGD-18016 | IRGAHH-18016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
897 | 1 | 1800 | IRGD-18012 | IRGD/P-18012 | P-1904 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
898 | 1 | 1800 | IRGD-18017 | IRGAH-18017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
899 | 1 | 1800 | IRGD-18017 | IRGAHH-18017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
900 | 1 | 1800 | IRGD-18018 | IRGD/P-18018 | C-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
901 | 1 | 1800 | IRGD-18018 | IRGAH-18018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
902 | 1 | 1800 | IRGD-18018 | IRGAHH-18018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
903 | 1 | 1800 | IRGD-18019 | IRGD/P-18019 | C-1901 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
904 | 1 | 1800 | IRGD-18019 | IRGAH-18019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
905 | 1 | 1800 | IRGD-18019 | IRGAHH-18019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
906 | 1 | 1800 | IRGD-18020 | IRGD/P-18020 | E-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA74 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
907 | 1 | 1800 | IRGD-18020 | IRGAH-18020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
908 | 1 | 1800 | IRGD-18020 | IRGAHH-18020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
909 | 1 | 1800 | IRGD-18021 | IRGD/P-18021 | V-1903 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
910 | 1 | 1800 | IRGD-18021 | IRGAH-18021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
911 | 1 | 1800 | IRGD-18021 | IRGAHH-18021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
912 | 1 | 1800 | IRGD-18022 | IRGD/P-18022 | V-1904 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
913 | 1 | 1800 | IRGD-18022 | IRGAH-18022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
914 | 1 | 1800 | IRGD-18022 | IRGAHH-18022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
915 | 1 | 1800 | IRGD-18023 | IRGD/P-18023 | V-1806 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
916 | 1 | 1800 | IRGD-18023 | IRGAH-18023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
917 | 1 | 1800 | IRGD-18023 | IRGAHH-18023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
918 | 1 | 1800 | IRGD-18026 | IRGD/P-18026 | C-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
919 | 1 | 1800 | IRGD-18026 | IRGAH-18026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
920 | 1 | 1800 | IRGD-18026 | IRGAHH-18026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
921 | 1 | 1800 | IRGD-18024 | IRGD/P-18024 | V-1803 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA75 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
922 | 1 | 1800 | IRGD-18024 | IRGAH-18024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
923 | 1 | 1800 | IRGD-18024 | IRGAHH-18024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
924 | 1 | 1800 | IRGD-18025 | IRGD/P-18025 | V-1803 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
925 | 1 | 1800 | IRGD-18025 | IRGAH-18025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
926 | 1 | 1800 | IRGD-18025 | IRGAHH-18025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
927 | 1 | 1800 | IRGD-18027 | IRGD/P-18027 | V-1902 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
928 | 1 | 1800 | IRGD-18027 | IRGAH-18027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
929 | 1 | 1800 | IRGD-18027 | IRGAHH-18027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
930 | 1 | 1800 | IRGD-18028 | IRGD/P-18028 | C-1901 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
931 | 1 | 1800 | IRGD-18028 | IRGAH-18028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
932 | 1 | 1800 | IRGD-18028 | IRGAHH-18028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
933 | 1 | 1800 | IRGD-18029 | IRGD/P-18029 | S-1802S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA77 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
934 | 1 | 1800 | IRGD-18029 | IRGAH-18029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
935 | 1 | 1800 | IRGD-18029 | IRGAHH-18029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
936 | 1 | 1800 | IRGD-18030 | IRGD/P-18030 | E-1802 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
937 | 1 | 1800 | IRGD-18030 | IRGAH-18030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
938 | 1 | 1800 | IRGD-18030 | IRGAHH-18030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
939 | 1 | 1800 | FD-18001 | FD-18001 | P-1814 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1206 | 0 | 1800 | FD-18001 | FAH-18001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
940 | 3 | 0000 | FD-18000 | FAH-18000B | Fire and Gas, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1100&1800 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
941 | 3 | 0003 | FD-18000 | FAH-18000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1100&1800 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
942 | 1 | 1800 | FD-18002 | FD-18002 | P-1801 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1210 | 0 | 1800 | FD-18002 | FAH-18002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
943 | 1 | 1800 | FD-18003 | FD-18003 | V-1801A |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA70 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1212 | 0 | 1800 | FD-18003 | FAH-18003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
944 | 1 | 1800 | FD-18004 | FD-18004 | V-1801B |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA70 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1214 | 0 | 1800 | FD-18004 | FAH-18004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
945 | 1 | 1800 | FD-18005 | FD-18005 | P-1802 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1216 | 0 | 1800 | FD-18005 | FAH-18005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
946 | 1 | 1800 | FD-18006 | FD-18006 | P-1810 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA71 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
947 | 1 | 1800 | FD-18006 | FAH-18006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
948 | 1 | 1800 | FD-18007 | FD-18007 | V-1901 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA73 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1220 | 0 | 1800 | FD-18007 | FAH-18007 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
949 | 1 | 1800 | TGD-18012 | TGD-18012 | P-1904 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1802 | AIR | NIS | FGDS | CRR | d | F | 1800JNA72 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
950 | 1 | 1800 | FD-18008 | FAH-18008 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
951 | 1 | 1800 | FD-18008 | FD-18008 | P-1903 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA72 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
952 | 1 | 1800 | FD-18009 | FAH-18009 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
953 | 1 | 1800 | FD-18010 | FD-18010 | P-1902 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA73 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
954 | 1 | 1800 | FD-18010 | FAH-18010 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
955 | 1 | 1800 | FD-18011 | FD-18011 | P-1901 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA73 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
956 | 1 | 1800 | FD-18011 | FAH-18011 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
957 | 1 | 1800 | FD-18012 | FD-18012 | P-1806 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA73 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
958 | 1 | 1800 | FD-18012 | FAH-18012 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
959 | 1 | 1800 | FD-18013 | FD-18013 | V-1806 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA75 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
960 | 1 | 1800 | FD-18013 | FAH-18013 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
961 | 1 | 1800 | FD-18014 | FD-18014 | V-1803 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA75 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
962 | 1 | 1800 | FD-18014 | FAH-18014 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
963 | 1 | 1800 | FD-18015 | FD-18015 | C-1902 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA74 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
964 | 1 | 1800 | FD-18015 | FAH-18015 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
965 | 1 | 1800 | FD-18016 | FD-18016 | V-1902 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1802 | AI | NIS | FGDS | CRR | d | F | 1800JNA77 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
966 | 1 | 1800 | FD-18016 | FAH-18016 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1239 | 0 | 1900 | TGD-19001 | TGD-19001 | D-1701 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1240 | 0 | 1900 | TGD-19001 | TGAH-19001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1241 | 0 | 1900 | TGD-19001 | TGAHH-19001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
967 | 3 | 0000 | TGD-19000 | TGA19000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 1900 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
968 | 3 | 0003 | TGD-19000 | TGA19000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1900 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
969 | 1 | 1900 | TGD-19002 | TGD-19002 | V-1906 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
970 | 1 | 1900 | TGD-19002 | TGAH-19002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
971 | 1 | 1900 | TGD-19002 | TGAHH-19002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
972 | 1 | 1900 | TGD-19003 | TGD-19003 | V-1907 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
973 | 1 | 1900 | TGD-19003 | TGAH-19003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
974 | 1 | 1900 | TGD-19003 | TGAHH-19003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
975 | 1 | 1900 | IRGD-19001 | IRGD/P-19001 | Cooling Tower | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1251 | 0 | 1900 | IRGD-19001 | IRGAH-19001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1252 | 0 | 1900 | IRGD-19001 | IRGAHH-19001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
976 | 3 | 0000 | IRGD-19000 | IRGA-19000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1900 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
977 | 3 | 0003 | IRGD-19000 | IRGA-19000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1900 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
978 | 1 | 1900 | IRGD-19002 | IRGD/P-19002 | Cooling Tower | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
979 | 1 | 1900 | IRGD-19002 | IRGAH-19002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
980 | 1 | 1900 | IRGD-19002 | IRGAHH-19002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
981 | 4 | 1900 | IRGD-19003 | IRGD/P-19003 | Cooling Tower | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
982 | 4 | 1900 | IRGD-19003 | IRGAH-19003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
983 | 4 | 1900 | IRGD-19003 | IRGAHH-19003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
984 | 1 | 1900 | IRGD-19004 | IRGD/P-19004 | V-1906 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
985 | 1 | 1900 | IRGD-19004 | IRGAH-19004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
986 | 1 | 1900 | IRGD-19004 | IRGAHH-19004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
987 | 1 | 1900 | IRGD-19005 | IRGD/P-19005 | V-1907 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
988 | 1 | 1900 | IRGD-19005 | IRGAH-19005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
989 | 1 | 1900 | IRGD-19005 | IRGAHH-19005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
990 | 2 | 1900 | FD-19001 | FD-19001 | P-1906 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1902 | AIR | NIS | FGDS | CRR | d | F | 1900JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1901 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA, Since there is no voting , for this Instrument, Signal connection is considered to be Redundant
991 | 1 | 1900 | FD-19001 | FAH-19001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
992 | 3 | 0000 | FD-19000 | FAH-19000B | Fire and Gas, Signal to CCR | FLAME GAS STATUS LAMP OF AREA 1900 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
993 | 3 | 0003 | FD-19000 | FAH-19000C | Signal connection through remote I/O | FLAME GAS STATUS LAMP OF AREA 1900 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
994 | 2 | 2600 | FD-26001 | FD-26001 | Y-2680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 | AI | NIS | FGDS | FRR | d | F | 2600JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1273 | 0 | 2600 | FD-26001 | FAH-26001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
995 | 2 | 2600 | FD-26002 | FD-26002 | Y-2680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 | AI | NIS | FGDS | FRR | d | F | 2600JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1275 | 0 | 2600 | FD-26002 | FAH-26002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
996 | 2 | 2600 | FD-26003 | FD-26003 | YX-2680/4 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1277 | 0 | 2600 | FD-26003 | FAH-26003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
997 | 2 | 2600 | FD-26004 | FD-26004 | Package Y1680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1279 | 0 | 2600 | FD-26004 | FAH-26004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
998 | 2 | 2600 | FD-26005 | FD-26005 | YTX-1680/14 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1281 | 0 | 2600 | FD-26005 | FAH-26005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
999 | 2 | 2600 | FD-26006 | FD-26006 | YX-1680/4 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1283 | 0 | 2600 | FD-26006 | FAH-26006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1000 | 4 | 2600 | HD-26001 | HD-26001 | Y-2680 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 | DI | NIS | FGDS | FRR | d | F | 4600JND70 | 1 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1285 | 0 | 2600 | HD-26001 | HA-26001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1001 | 3 | 0000 | HD-26000 | HA-26000B | Smoke, Signal to CCR | HEAT DETECTOR STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1002 | 3 | 0003 | HD-26000 | HA-26000C | Signal connection through remote I/O | HEAT DETECTOR STATUS LAMP OF FIRE ZONE 1600,2600,3600,4600 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1003 | 4 | 2600 | HD-26002 | HD-26002 | YTX-2680/14 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 | DI | NIS | FGDS | FRR | d | F | 4600JND70 | 2 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2601 | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1289 | 0 | 2600 | HD-26002 | HA-26002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1004 | 2 | 2600 | HD-26003 | HD-26003 | YX-2680/4 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1291 | 0 | 2600 | HD-26003 | HA-26003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1005 | 2 | 2600 | HD-26004 | HD-26004 | Y-1680 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1293 | 0 | 2600 | HD-26004 | HA-26004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1006 | 2 | 2600 | HD-26005 | HD-26005 | YTX-1680/14 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1295 | 0 | 2600 | HD-26005 | HA-26005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1007 | 2 | 2600 | HD-26006 | HD-26006 | YX-1680/4 |  | Heat Detector (Open Area | ESBR-HS-LYT-2602 (Rev.1) |  |  | FGDS | FRR | d | F | 2600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1297 | 0 | 2600 | HD-26006 | HA-26006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1008 | 2 | 3600 | FD-36001 | FD-36001 | Y-4660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 | AI | NIS | FGDS | FRR | d | F | 3600JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1299 | 0 | 3600 | FD-36001 | FAH-36001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1009 | 2 | 3600 | FD-36002 | FD-36002 | Y-4660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 | AI | NIS | FGDS | FRR | d | F | 3600JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1301 | 0 | 3600 | FD-36002 | FAH-36002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1010 | 2 | 3600 | FD-36003 | FD-36003 | Y-4660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 | AI | NIS | FGDS | FRR | d | F | 3600JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1303 | 0 | 3600 | FD-36003 | FAH-36003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1011 | 2 | 3600 | FD-36004 | FD-36004 | Y-3660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 | AI | NIS | FGDS | FRR | d | F | 3600JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1305 | 0 | 3600 | FD-36004 | FAH-36004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1012 | 2 | 3600 | FD-36005 | FD-36005 | Y-3660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1307 | 0 | 3600 | FD-36005 | FAH-36005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1013 | 2 | 3600 | FD-36006 | FD-36006 | Y-3660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1309 | 0 | 3600 | FD-36006 | FAH-36006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1014 | 2 | 3600 | HD-36001 | HD-36001 | Y-4660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1311 | 0 | 3600 | HD-36001 | HA-36001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1015 | 2 | 3600 | HD-36002 | HD-36002 | Y-4660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1313 | 0 | 3600 | HD-36002 | HA-36002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1016 | 2 | 3600 | HD-36003 | HD-36003 | Y-4660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1315 | 0 | 3600 | HD-36003 | HA-36003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1017 | 2 | 3600 | HD-36004 | HD-36004 | Y-3660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1317 | 0 | 3600 | HD-36004 | HA-36004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1018 | 2 | 3600 | HD-36005 | HD-36005 | Y-3660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1319 | 0 | 3600 | HD-36005 | HA-36005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1019 | 2 | 3600 | HD-36006 | HD-36006 | Y-3660 |  | Heat Detector (Open Area | ESBR-HS-LYT-3602 (Rev.1) |  |  | FGDS | FRR | d | F | 3600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1321 | 0 | 3600 | HD-36006 | HA-36006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1020 | 2 | 4600 | FD-46001 | FD-46001 | Y-4680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602 | AI | NIS | FGDS | FRR | d | F | 2600JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1323 | 0 | 4600 | FD-46001 | FAH-46001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1021 | 2 | 4600 | FD-46002 | FD-46002 | Y-4680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602 | AI | NIS | FGDS | FRR | d | F | 2600JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1325 | 0 | 4600 | FD-46002 | FAH-46002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1022 | 2 | 4600 | FD-46003 | FD-46003 | YX-4680/4 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1327 | 0 | 4600 | FD-46003 | FAH-46003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1023 | 2 | 4600 | FD-46004 | FD-46004 | Y-3680 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1329 | 0 | 4600 | FD-46004 | FAH-46004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1024 | 2 | 4600 | FD-46005 | FD-46005 | YTX-3680/14 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1331 | 0 | 4600 | FD-46005 | FAH-46005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1025 | 2 | 4600 | FD-46006 | FD-46006 | YX-3680/4 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1333 | 0 | 4600 | FD-46006 | FAH-46006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1026 | 4 | 4600 | HD-46001 | HD-46001 | Y-4680 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602 | DI | NIS | FGDS | FRR | d | F | 4600JND70 | 3 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1335 | 0 | 4600 | HD-46001 | HA-46001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1027 | 4 | 4600 | HD-46002 | HD-46002 | YTX-4680/14 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602 | DI | NIS | FGDS | FRR | d | F | 4600JND70 | 4 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-4601 | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1337 | 0 | 4600 | HD-46002 | HA-46002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1028 | 2 | 4600 | HD-46003 | HD-46003 | YX-4680/4 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1339 | 0 | 4600 | HD-46003 | HA-46003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1029 | 2 | 4600 | HD-46004 | HD-46004 | Y-3680 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1341 | 0 | 4600 | HD-46004 | HA-46004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1030 | 2 | 4600 | HD-46005 | HD-46005 | YTX-3680/14 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1343 | 0 | 4600 | HD-46005 | HA-46005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1031 | 2 | 4600 | HD-46006 | HD-46006 | YX-3680/4 |  | Heat Detector (Open Area | ESBR-HS-LYT-4602(Rev.1) |  |  | FGDS | FRR | d | F | 4600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
1345 | 0 | 4600 | HD-46006 | HA-46006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1032 | 1 | 1400 | TGD-14001 | TGD-14001 | K-1401A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1347 | 0 | 1400 | TGD-14001 | TGAH-14001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1348 | 0 | 1400 | TGD-14001 | TGAHH-14001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1033 | 3 | 0000 | TGD-14000 | TGA14000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 1400 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1034 | 3 | 0003 | TGD-14000 | TGA14000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1400 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1035 | 1 | 1400 | TGD-14002 | TGD-14002 | K-1401S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1352 | 0 | 1400 | TGD-14002 | TGAH-14002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1353 | 0 | 1400 | TGD-14002 | TGAHH-14002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1036 | 1 | 1400 | TGD-14003 | TGD-14003 | K-1401B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1355 | 0 | 1400 | TGD-14003 | TGAH-14003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1356 | 0 | 1400 | TGD-14003 | TGAHH-14003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1037 | 1 | 1400 | TGD-14004 | TGD-14004 | P-1403 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1358 | 0 | 1400 | TGD-14004 | TGAH-14004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1359 | 0 | 1400 | TGD-14004 | TGAHH-14004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1038 | 1 | 1400 | TGD-14005 | TGD-14005 | E-1404 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1361 | 0 | 1400 | TGD-14005 | TGAH-14005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1362 | 0 | 1400 | TGD-14005 | TGAHH-14005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1039 | 1 | 1400 | TGD-14006 | TGD-14006 | P-1412 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1364 | 0 | 1400 | TGD-14006 | TGAH-14006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1365 | 0 | 1400 | TGD-14006 | TGAHH-14006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1040 | 1 | 1400 | TGD-14007 | TGD-14007 | V-1406S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1367 | 0 | 1400 | TGD-14007 | TGAH-14007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1368 | 0 | 1400 | TGD-14007 | TGAHH-14007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1041 | 1 | 1400 | TGD-14008 | TGD-14008 | V-1406 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1370 | 0 | 1400 | TGD-14008 | TGAH-14008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1371 | 0 | 1400 | TGD-14008 | TGAHH-14008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1042 | 1 | 1400 | TGD-14009 | TGD-14009 | P-2403 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1373 | 0 | 1400 | TGD-14009 | TGAH-14009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1374 | 0 | 1400 | TGD-14009 | TGAHH-14009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1043 | 1 | 1400 | TGD-14010 | TGD-14010 | V-2406 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1376 | 0 | 1400 | TGD-14010 | TGAH-14010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1377 | 0 | 1400 | TGD-14010 | TGAHH-14010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1044 | 1 | 1400 | TGD-14011 | TGD-14011 | V-1401 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1379 | 0 | 1400 | TGD-14011 | TGAH-14011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1380 | 0 | 1400 | TGD-14011 | TGAHH-14011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1045 | 1 | 1400 | TGD-14012 | TGD-14012 | V-1401S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1382 | 0 | 1400 | TGD-14012 | TGAH-14012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1383 | 0 | 1400 | TGD-14012 | TGAHH-14012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1046 | 1 | 1400 | TGD-14013 | TGD-14013 | V-1403 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1385 | 0 | 1400 | TGD-14013 | TGAH-14013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1386 | 0 | 1400 | TGD-14013 | TGAHH-14013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1047 | 1 | 1400 | TGD-14014 | TGD-14014 | V-1402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1388 | 0 | 1400 | TGD-14014 | TGAH-14014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1389 | 0 | 1400 | TGD-14014 | TGAHH-14014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1048 | 1 | 1400 | TGD-14015 | TGD-14015 | V-1402S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1391 | 0 | 1400 | TGD-14015 | TGAH-14015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1392 | 0 | 1400 | TGD-14015 | TGAHH-14015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1049 | 1 | 1400 | TGD-14016 | TGD-14016 | V-1404 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1394 | 0 | 1400 | TGD-14016 | TGAH-14016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1395 | 0 | 1400 | TGD-14016 | TGAHH-14016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1050 | 1 | 1400 | TGD-14017 | TGD-14017 | V-1407S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1397 | 0 | 1400 | TGD-14017 | TGAH-14017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1398 | 0 | 1400 | TGD-14017 | TGAHH-14017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1051 | 1 | 1400 | TGD-14018 | TGD-14018 | V-1407 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1400 | 0 | 1400 | TGD-14018 | TGAH-14018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1401 | 0 | 1400 | TGD-14018 | TGAHH-14018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1052 | 1 | 1400 | TGD-14019 | TGD-14019 | V-1408A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1403 | 0 | 1400 | TGD-14019 | TGAH-14019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1404 | 0 | 1400 | TGD-14019 | TGAHH-14019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1053 | 1 | 1400 | TGD-14020 | TGD-14020 | V-1408S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1406 | 0 | 1400 | TGD-14020 | TGAH-14020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1407 | 0 | 1400 | TGD-14020 | TGAHH-14020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1054 | 1 | 1400 | TGD-14021 | TGD-14021 | V-1408B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1409 | 0 | 1400 | TGD-14021 | TGAH-14021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1410 | 0 | 1400 | TGD-14021 | TGAHH-14021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1055 | 1 | 1400 | TGD-14022 | TGD-14022 | V-1412 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1412 | 0 | 1400 | TGD-14022 | TGAH-14022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1413 | 0 | 1400 | TGD-14022 | TGAHH-14022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1056 | 1 | 1400 | TGD-14023 | TGD-14023 | V-2401 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1415 | 0 | 1400 | TGD-14023 | TGAH-14023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1416 | 0 | 1400 | TGD-14023 | TGAHH-14023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1057 | 1 | 1400 | TGD-14024 | TGD-14024 | V-2401S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1418 | 0 | 1400 | TGD-14024 | TGAH-14024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1419 | 0 | 1400 | TGD-14024 | TGAHH-14024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1058 | 1 | 1400 | TGD-14025 | TGD-14025 | V-2403 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1421 | 0 | 1400 | TGD-14025 | TGAH-14025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1422 | 0 | 1400 | TGD-14025 | TGAHH-14025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1059 | 1 | 1400 | TGD-14026 | TGD-14026 | V-2402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1424 | 0 | 1400 | TGD-14026 | TGAH-14026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1425 | 0 | 1400 | TGD-14026 | TGAHH-14026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1060 | 1 | 1400 | TGD-14027 | TGD-14027 | V-2402S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1427 | 0 | 1400 | TGD-14027 | TGAH-14027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1428 | 0 | 1400 | TGD-14027 | TGAHH-14027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1061 | 1 | 1400 | TGD-14028 | TGD-14028 | V-2404 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1430 | 0 | 1400 | TGD-14028 | TGAH-14028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1431 | 0 | 1400 | TGD-14028 | TGAHH-14028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1062 | 1 | 1400 | TGD-14029 | TGD-14029 | V-2407 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1433 | 0 | 1400 | TGD-14029 | TGAH-14029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1434 | 0 | 1400 | TGD-14029 | TGAHH-14029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1063 | 1 | 1400 | TGD-14030 | TGD-14030 | V-2407S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1436 | 0 | 1400 | TGD-14030 | TGAH-14030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1437 | 0 | 1400 | TGD-14030 | TGAHH-14030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1064 | 1 | 1400 | TGD-14031 | TGD-14031 | V-1405 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1439 | 0 | 1400 | TGD-14031 | TGAH-14031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1440 | 0 | 1400 | TGD-14031 | TGAHH-14031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1065 | 1 | 1400 | TGD-14032 | TGD-14032 | V-1405S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1442 | 0 | 1400 | TGD-14032 | TGAH-14032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1443 | 0 | 1400 | TGD-14032 | TGAHH-14032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1066 | 1 | 1400 | TGD-14033 | TGD-14033 | E-1401A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1445 | 0 | 1400 | TGD-14033 | TGAH-14033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1446 | 0 | 1400 | TGD-14033 | TGAHH-14033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1067 | 1 | 1400 | TGD-14034 | TGD-14034 | E-1401B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1448 | 0 | 1400 | TGD-14034 | TGAH-14034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1449 | 0 | 1400 | TGD-14034 | TGAHH-14034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1068 | 1 | 1400 | TGD-14035 | TGD-14035 | E-1401C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1451 | 0 | 1400 | TGD-14035 | TGAH-14035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1452 | 0 | 1400 | TGD-14035 | TGAHH-14035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1069 | 1 | 1400 | TGD-14036 | TGD-14036 | E-1401AS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1454 | 0 | 1400 | TGD-14036 | TGAH-14036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1455 | 0 | 1400 | TGD-14036 | TGAHH-14036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1070 | 1 | 1400 | TGD-14037 | TGD-14037 | E-1401BS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1457 | 0 | 1400 | TGD-14037 | TGAH-14037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1458 | 0 | 1400 | TGD-14037 | TGAHH-14037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1071 | 1 | 1400 | TGD-14038 | TGD-14038 | E-1401CS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1460 | 0 | 1400 | TGD-14038 | TGAH-14038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1461 | 0 | 1400 | TGD-14038 | TGAHH-14038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1072 | 1 | 1400 | TGD-14039 | TGD-14039 | V-1406 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1463 | 0 | 1400 | TGD-14039 | TGAH-14039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1464 | 0 | 1400 | TGD-14039 | TGAHH-14039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1073 | 1 | 1400 | TGD-14040 | TGD-14040 | V-1406S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1466 | 0 | 1400 | TGD-14040 | TGAH-14040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1467 | 0 | 1400 | TGD-14040 | TGAHH-14040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1074 | 1 | 1400 | TGD-14041 | TGD-14041 | V-2406 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1469 | 0 | 1400 | TGD-14041 | TGAH-14041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1470 | 0 | 1400 | TGD-14041 | TGAHH-14041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1075 | 1 | 1400 | TGD-14042 | TGD-14042 | V-2406S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1472 | 0 | 1400 | TGD-14042 | TGAH-14042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1473 | 0 | 1400 | TGD-14042 | TGAHH-14042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1076 | 1 | 1400 | TGD-14043 | TGD-14043 | E-1405S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1475 | 0 | 1400 | TGD-14043 | TGAH-14043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1476 | 0 | 1400 | TGD-14043 | TGAHH-14043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1077 | 1 | 1400 | TGD-14044 | TGD-14044 | E-1405 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1478 | 0 | 1400 | TGD-14044 | TGAH-14044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1479 | 0 | 1400 | TGD-14044 | TGAHH-14044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1480 | 0 | 1400 | TGD-14045 | TGD-14045 | E-1402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA79 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1481 | 0 | 1400 | TGD-14045 | TGAH-14045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1482 | 0 | 1400 | TGD-14045 | TGAHH-14045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1078 | 1 | 1400 | TGD-14046 | TGD-14046 | V-2406S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1484 | 0 | 1400 | TGD-14046 | TGAH-14046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1485 | 0 | 1400 | TGD-14046 | TGAHH-14046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1079 | 1 | 1400 | TGD-14047 | TGD-14047 | E-1403A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1487 | 0 | 1400 | TGD-14047 | TGAH-14047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1488 | 0 | 1400 | TGD-14047 | TGAHH-14047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1080 | 1 | 1400 | TGD-14048 | TGD-14048 | E-1403B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1490 | 0 | 1400 | TGD-14048 | TGAH-14048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1491 | 0 | 1400 | TGD-14048 | TGAHH-14048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1081 | 1 | 1400 | TGD-14049 | TGD-14049 | E-1403S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1493 | 0 | 1400 | TGD-14049 | TGAH-14049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1494 | 0 | 1400 | TGD-14049 | TGAHH-14049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1082 | 1 | 1400 | TGD-14050 | TGD-14050 | V-1409 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1496 | 0 | 1400 | TGD-14050 | TGAH-14050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1497 | 0 | 1400 | TGD-14050 | TGAHH-14050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1083 | 1 | 1400 | TGD-14051 | TGD-14051 | V-1409S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1499 | 0 | 1400 | TGD-14051 | TGAH-14051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1500 | 0 | 1400 | TGD-14051 | TGAHH-14051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1084 | 1 | 1400 | TGD-14052 | TGD-14052 | E-1404 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1502 | 0 | 1400 | TGD-14052 | TGAH-14052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1503 | 0 | 1400 | TGD-14052 | TGAHH-14052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1085 | 1 | 1400 | TGD-14053 | TGD-14053 | V-2405 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1505 | 0 | 1400 | TGD-14053 | TGAH-14053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1506 | 0 | 1400 | TGD-14053 | TGAHH-14053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1086 | 1 | 1400 | TGD-14054 | TGD-14054 | V-2405S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1508 | 0 | 1400 | TGD-14054 | TGAH-14054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1509 | 0 | 1400 | TGD-14054 | TGAHH-14054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1087 | 1 | 1400 | TGD-14055 | TGD-14055 | E-2401A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1511 | 0 | 1400 | TGD-14055 | TGAH-14055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1512 | 0 | 1400 | TGD-14055 | TGAHH-14055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1088 | 1 | 1400 | TGD-14056 | TGD-14056 | E-2401B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1514 | 0 | 1400 | TGD-14056 | TGAH-14056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1515 | 0 | 1400 | TGD-14056 | TGAHH-14056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1089 | 1 | 1400 | TGD-14057 | TGD-14057 | E-2401C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1517 | 0 | 1400 | TGD-14057 | TGAH-14057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1518 | 0 | 1400 | TGD-14057 | TGAHH-14057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1090 | 1 | 1400 | TGD-14058 | TGD-14058 | E-2401AS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1520 | 0 | 1400 | TGD-14058 | TGAH-14058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1521 | 0 | 1400 | TGD-14058 | TGAHH-14058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1091 | 1 | 1400 | TGD-14059 | TGD-14059 | E-2401BS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1523 | 0 | 1400 | TGD-14059 | TGAH-14059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1524 | 0 | 1400 | TGD-14059 | TGAHH-14059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1092 | 1 | 1400 | TGD-14060 | TGD-14060 | E-2401CS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1526 | 0 | 1400 | TGD-14060 | TGAH-14060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1527 | 0 | 1400 | TGD-14060 | TGAHH-14060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1528 | 0 | 1400 | TGD-14061 | TGD-14061 | E-2402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA79 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1529 | 0 | 1400 | TGD-14061 | TGAH-14061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1530 | 0 | 1400 | TGD-14061 | TGAHH-14061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1093 | 1 | 1400 | TGD-14062 | TGD-14062 | E-2405 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1532 | 0 | 1400 | TGD-14062 | TGAH-14062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1533 | 0 | 1400 | TGD-14062 | TGAHH-14062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1094 | 1 | 1400 | TGD-14063 | TGD-14063 | E-2405S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1535 | 0 | 1400 | TGD-14063 | TGAH-14063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1536 | 0 | 1400 | TGD-14063 | TGAHH-14063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1095 | 1 | 1400 | TGD-14064 | TGD-14064 | E-1401AS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1096 | 1 | 1400 | TGD-14064 | TGAH-14064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1097 | 1 | 1400 | TGD-14064 | TGAHH-14064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1098 | 1 | 1400 | TGD-14065 | TGD-14065 | E-1401BS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1099 | 1 | 1400 | TGD-14065 | TGAH-14065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1100 | 1 | 1400 | TGD-14065 | TGAHH-14065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1101 | 1 | 1400 | TGD-14066 | TGD-14066 | E-1401CS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1102 | 1 | 1400 | TGD-14066 | TGAH-14066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1103 | 1 | 1400 | TGD-14066 | TGAHH-14066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1104 | 1 | 1400 | TGD-14067 | TGD-14067 | E-1401A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1105 | 1 | 1400 | TGD-14067 | TGAH-14067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1106 | 1 | 1400 | TGD-14067 | TGAHH-14067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1107 | 1 | 1400 | TGD-14068 | TGD-14068 | E-1401B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1108 | 1 | 1400 | TGD-14068 | TGAH-14068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1109 | 1 | 1400 | TGD-14068 | TGAHH-14068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1110 | 1 | 1400 | TGD-14069 | TGD-14069 | E-1401C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1111 | 1 | 1400 | TGD-14069 | TGAH-14069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1112 | 1 | 1400 | TGD-14069 | TGAHH-14069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1113 | 1 | 1400 | TGD-14070 | TGD-14070 | E-2401A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1114 | 1 | 1400 | TGD-14070 | TGAH-14070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1115 | 1 | 1400 | TGD-14070 | TGAHH-14070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1116 | 1 | 1400 | TGD-14071 | TGD-14071 | E-2401B |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1117 | 1 | 1400 | TGD-14071 | TGAH-14071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1118 | 1 | 1400 | TGD-14071 | TGAHH-14071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1119 | 1 | 1400 | TGD-14072 | TGD-14072 | E-2401C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1120 | 1 | 1400 | TGD-14072 | TGAH-14072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1121 | 1 | 1400 | TGD-14072 | TGAHH-14072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1122 | 1 | 1400 | TGD-14073 | TGD-14073 | E-2401AS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1123 | 1 | 1400 | TGD-14073 | TGAH-14073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1124 | 1 | 1400 | TGD-14073 | TGAHH-14073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1125 | 1 | 1400 | TGD-14074 | TGD-14074 | E-2401BS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1126 | 1 | 1400 | TGD-14074 | TGAH-14074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1127 | 1 | 1400 | TGD-14074 | TGAHH-14074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1128 | 1 | 1400 | TGD-14075 | TGD-14075 | E-2401CS |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1129 | 1 | 1400 | TGD-14075 | TGAH-14075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1130 | 1 | 1400 | TGD-14075 | TGAHH-14075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1131 | 1 | 1400 | TGD-14076 | TGD-14076 | E-1402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA81 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1132 | 1 | 1400 | TGD-14076 | TGAH-14076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1133 | 1 | 1400 | TGD-14076 | TGAHH-14076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1134 | 1 | 1400 | TGD-14077 | TGD-14077 | E-2402 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1135 | 1 | 1400 | TGD-14077 | TGAH-14077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1136 | 1 | 1400 | TGD-14077 | TGAHH-14077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1137 | 1 | 1400 | IRGD-14001 | IRGD/OPT-14001 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1138 | 1 | 1400 | IRGD-14001 | IRGD/OPR-14001 | K-1401A/B/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1581 | 0 | 1400 | IRGD-14001 | IRGAH-14001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1582 | 0 | 1400 | IRGD-14001 | IRGAHH-14001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1139 | 3 | 0000 | IRGD-14000 | IRGA-14000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1400 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1140 | 3 | 0003 | IRGD-14000 | IRGA-14000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1400 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1141 | 1 | 1400 | IRGD-14002 | IRGD/OPT-14002 | K-1401A/B/S, V-1408A/B/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1142 | 1 | 1400 | IRGD-14002 | IRGD/OPR-14002 | K-1401A/B/S, V-1408A/B/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1587 | 0 | 1400 | IRGD-14002 | IRGAH-14002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1588 | 0 | 1400 | IRGD-14002 | IRGAHH-14002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1143 | 1 | 1400 | IRGD-14003 | IRGD/OPT-14003 | E-1403A/B/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1144 | 1 | 1400 | IRGD-14003 | IRGD/OPR-14003 | E-1403A/B/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA78 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1591 | 0 | 1400 | IRGD-14003 | IRGAH-14003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1592 | 0 | 1400 | IRGD-14003 | IRGAHH-14003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1145 | 1 | 1400 | IRGD-14004 | IRGD/P-14004 | P-1403 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1594 | 0 | 1400 | IRGD-14004 | IRGAH-14004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1595 | 0 | 1400 | IRGD-14004 | IRGAHH-14004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1146 | 1 | 1400 | IRGD-14005 | IRGD/P-14005 | E-1404 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1597 | 0 | 1400 | IRGD-14005 | IRGAH-14005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1598 | 0 | 1400 | IRGD-14005 | IRGAHH-14005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1147 | 1 | 1400 | IRGD-14006 | IRGD/P-14006 | P-1412 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1600 | 0 | 1400 | IRGD-14006 | IRGAH-14006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1601 | 0 | 1400 | IRGD-14006 | IRGAHH-14006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1148 | 1 | 1400 | IRGD-14007 | IRGD/OPT-14007 | V-2406/S, V-1406/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1149 | 2 | 1400 | IRGD-14007 | IRGD/OPR-14007 | V-2406/S, V-1406/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 14 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1604 | 0 | 1400 | IRGD-14007 | IRGAH-14007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1605 | 0 | 1400 | IRGD-14007 | IRGAHH-14007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1150 | 1 | 1400 | IRGD-14008 | IRGD/P-14008 | E-2405 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1607 | 0 | 1400 | IRGD-14008 | IRGAH-14008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1608 | 0 | 1400 | IRGD-14008 | IRGAHH-14008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1151 | 1 | 1400 | IRGD-14009 | IRGD/P-14009 | P-2403 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1610 | 0 | 1400 | IRGD-14009 | IRGAH-14009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1611 | 0 | 1400 | IRGD-14009 | IRGAHH-14009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1152 | 1 | 1400 | IRGD-14010 | IRGD/P-14010 | E-1402 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA79 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1613 | 0 | 1400 | IRGD-14010 | IRGAH-14010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1614 | 0 | 1400 | IRGD-14010 | IRGAHH-14010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1153 | 1 | 1400 | IRGD-14011 | IRGD/OPT-14011 | V-1401 | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1154 | 1 | 1400 | IRGD-14011 | IRGD/OPR-14011 | V-1401 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1617 | 0 | 1400 | IRGD-14011 | IRGAH-14011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1618 | 0 | 1400 | IRGD-14011 | IRGAHH-14011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1155 | 1 | 1400 | IRGD-14012 | IRGD/OPT-14012 | V-1401S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1156 | 1 | 1400 | IRGD-14012 | IRGD/OPR-14012 | V-1401S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1621 | 0 | 1400 | IRGD-14012 | IRGAH-14012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1622 | 0 | 1400 | IRGD-14012 | IRGAHH-14012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1157 | 1 | 1400 | IRGD-14013 | IRGD/OPT-14013 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1158 | 1 | 1400 | IRGD-14013 | IRGD/OPR-14013 | V-1403 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1625 | 0 | 1400 | IRGD-14013 | IRGAH-14013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1626 | 0 | 1400 | IRGD-14013 | IRGAHH-14013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1159 | 1 | 1400 | IRGD-14014 | IRGD/P-14014 | V-1402 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1628 | 0 | 1400 | IRGD-14014 | IRGAH-14014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1629 | 0 | 1400 | IRGD-14014 | IRGAHH-14014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1160 | 1 | 1400 | IRGD-14015 | IRGD/P-14015 | V-1402S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1631 | 0 | 1400 | IRGD-14015 | IRGAH-14015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1632 | 0 | 1400 | IRGD-14015 | IRGAHH-14015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1161 | 1 | 1400 | IRGD-14016 | IRGD/P-14016 | V-1404 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1634 | 0 | 1400 | IRGD-14016 | IRGAH-14016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1635 | 0 | 1400 | IRGD-14016 | IRGAHH-14016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1162 | 1 | 1400 | IRGD-14017 | IRGD/OPT-14017 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1163 | 1 | 1400 | IRGD-14017 | IRGD/OPR-14017 | V-1407S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1638 | 0 | 1400 | IRGD-14017 | IRGAH-14017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1639 | 0 | 1400 | IRGD-14017 | IRGAHH-14017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1164 | 1 | 1400 | IRGD-14018 | IRGD/OPT-14018 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1165 | 1 | 1400 | IRGD-14018 | IRGD/OPR-14018 | V-1407 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA72 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1642 | 0 | 1400 | IRGD-14018 | IRGAH-14018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1643 | 0 | 1400 | IRGD-14018 | IRGAHH-14018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1166 | 1 | 1400 | IRGD-14019 | IRGD/OPT-14019 | E-2401A/AS, E-1401A/AS, V-2405/S, V-1405/S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1167 | 1 | 1400 | IRGD-14019 | IRGD/OPR-14019 | E-2401A/AS, E-1401A/AS, V-2405/S, V-1405/S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1646 | 0 | 1400 | IRGD-14019 | IRGAH-14019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1647 | 0 | 1400 | IRGD-14019 | IRGAHH-14019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1168 | 1 | 1400 | IRGD-14020 | IRGD/OPT-14020 | E-2401C/CS/B/BS, E-1401C/CS/B/BS | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1169 | 1 | 1400 | IRGD-14020 | IRGD/OPR-14020 | E-2401C/CS/B/BS, E-1401C/CS/B/BS | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA77 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1650 | 0 | 1400 | IRGD-14020 | IRGAH-14020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1651 | 0 | 1400 | IRGD-14020 | IRGAHH-14020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1170 | 1 | 1400 | IRGD-14021 | IRGD/OPT-14021 | E-1401A/AS/B/BS, E-2401A/AS/B/BS | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1171 | 2 | 1400 | IRGD-14021 | IRGD/OPR-14021 | E-1401A/AS/B/BS, E-2401A/AS/B/BS | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1654 | 0 | 1400 | IRGD-14021 | IRGAH-14021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1655 | 0 | 1400 | IRGD-14021 | IRGAHH-14021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1172 | 1 | 1400 | IRGD-14022 | IRGD/P-14022 | V-1412 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA71 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1657 | 0 | 1400 | IRGD-14022 | IRGAH-14022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1658 | 0 | 1400 | IRGD-14022 | IRGAHH-14022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1173 | 1 | 1400 | IRGD-14023 | IRGD/OPT-14023 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1174 | 1 | 1400 | IRGD-14023 | IRGD/OPR-14023 | V-2401 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1661 | 0 | 1400 | IRGD-14023 | IRGAH-14023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1662 | 0 | 1400 | IRGD-14023 | IRGAHH-14023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1175 | 1 | 1400 | IRGD-14024 | IRGD/OPT-14024 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1176 | 1 | 1400 | IRGD-14024 | IRGD/OPR-14024 | V-2401S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1665 | 0 | 1400 | IRGD-14024 | IRGAH-14024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1666 | 0 | 1400 | IRGD-14024 | IRGAHH-14024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1177 | 1 | 1400 | IRGD-14025 | IRGD/OPT-14025 |  | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1178 | 1 | 1400 | IRGD-14025 | IRGD/OPR-14025 | V-2403 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1669 | 0 | 1400 | IRGD-14025 | IRGAH-14025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1670 | 0 | 1400 | IRGD-14025 | IRGAHH-14025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1179 | 1 | 1400 | IRGD-14026 | IRGD/P-14026 | V-2402 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1672 | 0 | 1400 | IRGD-14026 | IRGAH-14026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1673 | 0 | 1400 | IRGD-14026 | IRGAHH-14026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1180 | 1 | 1400 | IRGD-14027 | IRGD/P-14027 | V-2402S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1675 | 0 | 1400 | IRGD-14027 | IRGAH-14027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1676 | 0 | 1400 | IRGD-14027 | IRGAHH-14027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1181 | 1 | 1400 | IRGD-14028 | IRGD/P-14028 | V-2404 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1678 | 0 | 1400 | IRGD-14028 | IRGAH-14028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1679 | 0 | 1400 | IRGD-14028 | IRGAHH-14028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1182 | 1 | 1400 | IRGD-14029 | IRGD/OPT-14029 | V-2407 | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1183 | 1 | 1400 | IRGD-14029 | IRGD/OPR-14029 | V-2407 | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1682 | 0 | 1400 | IRGD-14029 | IRGAH-14029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1683 | 0 | 1400 | IRGD-14029 | IRGAHH-14029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1184 | 1 | 1400 | IRGD-14030 | IRGD/OPT-14030 | V-2407S | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1185 | 1 | 1400 | IRGD-14030 | IRGD/OPR-14030 | V-2407S | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA73 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1686 | 0 | 1400 | IRGD-14030 | IRGAH-14030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1687 | 0 | 1400 | IRGD-14030 | IRGAHH-14030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1186 | 1 | 1400 | IRGD-14031 | IRGD/P-14031 | E-2405S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1689 | 0 | 1400 | IRGD-14031 | IRGAH-14031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1690 | 0 | 1400 | IRGD-14031 | IRGAHH-14031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1187 | 1 | 1400 | IRGD-14032 | IRGD/OPT-14032 | E-2402, E-1402, E-2401C/CS, E-1401C/CS | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 |  |  |  |  | d | F
1188 | 2 | 1400 | IRGD-14032 | IRGD/OPR-14032 | E-2402, E-1402, E-2401C/CS, E-1401C/CS | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA80 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1693 | 0 | 1400 | IRGD-14032 | IRGAH-14032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1694 | 0 | 1400 | IRGD-14032 | IRGAHH-14032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1189 | 1 | 1400 | IRGD-14033 | IRGD/P-14033 | E-1405S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1696 | 0 | 1400 | IRGD-14033 | IRGAH-14033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1697 | 0 | 1400 | IRGD-14033 | IRGAHH-14033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1190 | 1 | 1400 | IRGD-14034 | IRGD/P-14034 | E-1405 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA74 | 13 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1699 | 0 | 1400 | IRGD-14034 | IRGAH-14034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1700 | 0 | 1400 | IRGD-14034 | IRGAHH-14034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1191 | 1 | 1400 | IRGD-14035 | IRGD/P-14035 | E-1404 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1702 | 0 | 1400 | IRGD-14035 | IRGAH-14035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1703 | 0 | 1400 | IRGD-14035 | IRGAHH-14035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1192 | 1 | 1400 | IRGD-14036 | IRGD/P-14036 | V-1409S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1705 | 0 | 1400 | IRGD-14036 | IRGAH-14036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1706 | 0 | 1400 | IRGD-14036 | IRGAHH-14036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1193 | 1 | 1400 | IRGD-14037 | IRGD/P-14037 | V-1409 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA75 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1708 | 0 | 1400 | IRGD-14037 | IRGAH-14037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1709 | 0 | 1400 | IRGD-14037 | IRGAHH-14037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1194 | 1 | 1400 | IRGD-14038 | IRGD/P-14038 | E-2402 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA79 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1711 | 0 | 1400 | IRGD-14038 | IRGAH-14038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1712 | 0 | 1400 | IRGD-14038 | IRGAHH-14038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1195 | 1 | 1400 | IRGD-14039 | IRGD/P-14039 | V-1406 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1714 | 0 | 1400 | IRGD-14039 | IRGAH-14039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1715 | 0 | 1400 | IRGD-14039 | IRGAHH-14039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1196 | 1 | 1400 | IRGD-14040 | IRGD/P-14040 | V-1406S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1717 | 0 | 1400 | IRGD-14040 | IRGAH-14040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1718 | 0 | 1400 | IRGD-14040 | IRGAHH-14040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1197 | 1 | 1400 | IRGD-14041 | IRGD/P-14041 | V-2406 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1720 | 0 | 1400 | IRGD-14041 | IRGAH-14041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1721 | 0 | 1400 | IRGD-14041 | IRGAHH-14041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1198 | 1 | 1400 | IRGD-14042 | IRGD/P-14042 | V-2406S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402 | AIR | NIS | FGDS | CRR | d | F | 1400JNA76 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1723 | 0 | 1400 | IRGD-14042 | IRGAH-14042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1724 | 0 | 1400 | IRGD-14042 | IRGAHH-14042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1725 | 0 | 1400 | IRGD-14043 | IRGD/OP-14043 | E-1405S | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1726 | 0 | 1400 | IRGD-14043 | IRGAH-14043 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1727 | 0 | 1400 | IRGD-14043 | IRGAHH-14043 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1728 | 0 | 1400 | IRGD-14044 | IRGD/OP-14044 | E-1405 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1729 | 0 | 1400 | IRGD-14044 | IRGAH-14044 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1730 | 0 | 1400 | IRGD-14044 | IRGAHH-14044 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1731 | 0 | 1400 | IRGD-14045 | IRGD/OP-14045 | E-1402 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA87 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1732 | 0 | 1400 | IRGD-14045 | IRGAH-14045 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1733 | 0 | 1400 | IRGD-14045 | IRGAHH-14045 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1734 | 0 | 1400 | IRGD-14046 | IRGD/OP-14046 | Y-1450-FUN | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1735 | 0 | 1400 | IRGD-14046 | IRGAH-14046 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1736 | 0 | 1400 | IRGD-14046 | IRGAHH-14046 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1737 | 0 | 1400 | IRGD-14047 | IRGD/OP-14047 | E-1403A | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA86 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1738 | 0 | 1400 | IRGD-14047 | IRGAH-14047 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1739 | 0 | 1400 | IRGD-14047 | IRGAHH-14047 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1740 | 0 | 1400 | IRGD-14048 | IRGD/OP-14048 | E-1403B | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA86 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1741 | 0 | 1400 | IRGD-14048 | IRGAH-14048 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1742 | 0 | 1400 | IRGD-14048 | IRGAHH-14048 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1743 | 0 | 1400 | IRGD-14049 | IRGD/OP-14049 | E-1403C | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA86 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1744 | 0 | 1400 | IRGD-14049 | IRGAH-14049 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1745 | 0 | 1400 | IRGD-14049 | IRGAHH-14049 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1746 | 0 | 1400 | IRGD-14050 | IRGD/OP-14050 | V-1409 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1747 | 0 | 1400 | IRGD-14050 | IRGAH-14050 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1748 | 0 | 1400 | IRGD-14050 | IRGAHH-14050 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1749 | 0 | 1400 | IRGD-14051 | IRGD/OP-14051 | V-1409S | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1750 | 0 | 1400 | IRGD-14051 | IRGAH-14051 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1751 | 0 | 1400 | IRGD-14051 | IRGAHH-14051 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1752 | 0 | 1400 | IRGD-14052 | IRGD/OP-14052 | E-1404 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1753 | 0 | 1400 | IRGD-14052 | IRGAH-14052 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1754 | 0 | 1400 | IRGD-14052 | IRGAHH-14052 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1755 | 0 | 1400 | IRGD-14053 | IRGD/OP-14053 | V-2405 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA83 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1756 | 0 | 1400 | IRGD-14053 | IRGAH-14053 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1757 | 0 | 1400 | IRGD-14053 | IRGAHH-14053 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1758 | 0 | 1400 | IRGD-14054 | IRGD/OP-14054 | V-2405S | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA82 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1759 | 0 | 1400 | IRGD-14054 | IRGAH-14054 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1760 | 0 | 1400 | IRGD-14054 | IRGAHH-14054 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1761 | 0 | 1400 | IRGD-14055 | IRGD/OP-14055 | E-2401A | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA83 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1762 | 0 | 1400 | IRGD-14055 | IRGAH-14055 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1763 | 0 | 1400 | IRGD-14055 | IRGAHH-14055 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1764 | 0 | 1400 | IRGD-14056 | IRGD/OP-14056 | E-2401B | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA83 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1765 | 0 | 1400 | IRGD-14056 | IRGAH-14056 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1766 | 0 | 1400 | IRGD-14056 | IRGAHH-14056 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1767 | 0 | 1400 | IRGD-14057 | IRGD/OP-14057 | E-2401C | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA83 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1768 | 0 | 1400 | IRGD-14057 | IRGAH-14057 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1769 | 0 | 1400 | IRGD-14057 | IRGAHH-14057 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1770 | 0 | 1400 | IRGD-14058 | IRGD/OP-14058 | E-2401AS | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA82 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1771 | 0 | 1400 | IRGD-14058 | IRGAH-14058 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1772 | 0 | 1400 | IRGD-14058 | IRGAHH-14058 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1773 | 0 | 1400 | IRGD-14059 | IRGD/OP-14059 | E-2401BS | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA82 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1774 | 0 | 1400 | IRGD-14059 | IRGAH-14059 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1775 | 0 | 1400 | IRGD-14059 | IRGAHH-14059 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1776 | 0 | 1400 | IRGD-14060 | IRGD/OP-14060 | E-2401CS | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA82 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1777 | 0 | 1400 | IRGD-14060 | IRGAH-14060 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1778 | 0 | 1400 | IRGD-14060 | IRGAHH-14060 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1779 | 0 | 1400 | IRGD-14061 | IRGD/OP-14061 | E-2402 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F | 1400JNA87 |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1780 | 0 | 1400 | IRGD-14061 | IRGAH-14061 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1781 | 0 | 1400 | IRGD-14061 | IRGAHH-14061 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1782 | 0 | 1400 | IRGD-14062 | IRGD/OP-14062 | E-2405 | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1783 | 0 | 1400 | IRGD-14062 | IRGAH-14062 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1784 | 0 | 1400 | IRGD-14062 | IRGAHH-14062 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1785 | 0 | 1400 | IRGD-14063 | IRGD/OP-14063 | E-2405S | Open Path Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-1402(Rev.0) |  |  | FGDS | CRR | d | F |  |  | 16-T-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1786 | 0 | 1400 | IRGD-14063 | IRGAH-14063 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1787 | 0 | 1400 | IRGD-14063 | IRGAHH-14063 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1199 | 1 | 1400 | FD-14001 | FD-14001 | K-1401B |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1789 | 0 | 1400 | FD-14001 | FAH-14001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1200 | 3 | 0000 | FD-14000 | FAH-14000B | Fire and Gas, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1400 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1201 | 3 | 0003 | FD-14000 | FA-14000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1400 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1202 | 1 | 1400 | FD-14002 | FD-14002 | K-1401B, V-1408B |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1793 | 0 | 1400 | FD-14002 | FAH-14002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1203 | 1 | 1400 | FD-14003 | FD-14003 | K-1401S |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1204 | 1 | 1400 | FD-14003 | FAH-14003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1205 | 1 | 1400 | FD-14004 | FD-14004 | K-1401S, V-1408S |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1206 | 1 | 1400 | FD-14004 | FAH-14004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1207 | 1 | 1400 | FD-14005 | FD-14005 | K-1401A |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA70 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1208 | 1 | 1400 | FD-14005 | FAH-14005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1209 | 1 | 1400 | FD-14006 | FD-14006 | K-1401A, V-1408A |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA70 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1210 | 1 | 1400 | FD-14006 | FAH-14006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1211 | 1 | 1400 | FD-14007 | FD-14007 | P-1413 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1402 | AI | NIS | FGDS | CRR | d | F | 1400JNA71 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1212 | 1 | 1400 | FD-14007 | FAH-14007 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1213 | 1 | 2300 | IRGD-23001 | IRGD/P- 23001 | R-2301 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1805 | 0 | 2300 | IRGD-23001 | IRGAH-23001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1806 | 0 | 2300 | IRGD-23001 | IRGAHH-23001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1214 | 3 | 0000 | IRGD-23001 | IRGA-23001B | Fire and Gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND13 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1215 | 2 | 0003 | IRGD-23001 | IRGA-23001C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1216 | 1 | 2300 | IRGD-23002 | IRGD/P- 23002 | R-2302 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1810 | 0 | 2300 | IRGD-23002 | IRGAH-23002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1811 | 0 | 2300 | IRGD-23002 | IRGAHH-23002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1217 | 1 | 2300 | IRGD-23003 | IRGD/P- 23003 | R-2303 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1813 | 0 | 2300 | IRGD-23003 | IRGAH-23003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1814 | 0 | 2300 | IRGD-23003 | IRGAHH-23003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1218 | 1 | 2300 | IRGD-23004 | IRGD/P- 23004 | R-2304 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1816 | 0 | 2300 | IRGD-23004 | IRGAH-23004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1817 | 0 | 2300 | IRGD-23004 | IRGAHH-23004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1219 | 1 | 2300 | IRGD-23005 | IRGD/P- 23005 | R-2305 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1819 | 0 | 2300 | IRGD-23005 | IRGAH-23005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1820 | 0 | 2300 | IRGD-23005 | IRGAHH-23005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1220 | 1 | 2300 | IRGD-23006 | IRGD/P- 23006 | R-2306 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1822 | 0 | 2300 | IRGD-23006 | IRGAH-23006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1823 | 0 | 2300 | IRGD-23006 | IRGAHH-23006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1221 | 1 | 2300 | IRGD-23007 | IRGD/P- 23007 | R-2307 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1825 | 0 | 2300 | IRGD-23007 | IRGAH-23007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1826 | 0 | 2300 | IRGD-23007 | IRGAHH-23007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1222 | 1 | 2300 | IRGD-23008 | IRGD/P- 23008 | R-2308 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1828 | 0 | 2300 | IRGD-23008 | IRGAH-23008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1829 | 0 | 2300 | IRGD-23008 | IRGAHH-23008 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1223 | 1 | 2300 | IRGD-23009 | IRGD/P- 23009 | R-2309 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1831 | 0 | 2300 | IRGD-23009 | IRGAH-23009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1832 | 0 | 2300 | IRGD-23009 | IRGAHH-23009 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1224 | 1 | 2300 | IRGD-23010 | IRGD/P- 23010 | R-2310 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1834 | 0 | 2300 | IRGD-23010 | IRGAH-23010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1835 | 0 | 2300 | IRGD-23010 | IRGAHH-23010 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1225 | 1 | 2300 | IRGD-23011 | IRGD/P- 23011 | R-2311 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1837 | 0 | 2300 | IRGD-23011 | IRGAH-23011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1838 | 0 | 2300 | IRGD-23011 | IRGAHH-23011 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1226 | 1 | 2300 | IRGD-23012 | IRGD/P- 23012 | R-2312 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1840 | 0 | 2300 | IRGD-23012 | IRGAH-23012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1841 | 0 | 2300 | IRGD-23012 | IRGAHH-23012 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1227 | 1 | 2300 | IRGD-23013 | IRGD/P- 23013 | R-2313 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1843 | 0 | 2300 | IRGD-23013 | IRGAH-23013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1844 | 0 | 2300 | IRGD-23013 | IRGAHH-23013 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1228 | 1 | 2300 | IRGD-23014 | IRGD/P- 23014 | R-2314 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1846 | 0 | 2300 | IRGD-23014 | IRGAH-23014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1847 | 0 | 2300 | IRGD-23014 | IRGAHH-23014 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1229 | 1 | 2300 | IRGD-23015 | IRGD/P- 23015 | V-2315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1849 | 0 | 2300 | IRGD-23015 | IRGAH-23015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1850 | 0 | 2300 | IRGD-23015 | IRGAHH-23015 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1230 | 1 | 2300 | IRGD-23016 | IRGD/P- 23016 | V-2317 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1852 | 0 | 2300 | IRGD-23016 | IRGAH-23016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1853 | 0 | 2300 | IRGD-23016 | IRGAHH-23016 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1231 | 1 | 2300 | IRGD-23017 | IRGD/P- 23017 | V-2317S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1855 | 0 | 2300 | IRGD-23017 | IRGAH-23017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1856 | 0 | 2300 | IRGD-23017 | IRGAHH-23017 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1232 | 1 | 2300 | IRGD-23018 | IRGD/P- 23018 | V-2319 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1858 | 0 | 2300 | IRGD-23018 | IRGAH-23018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1859 | 0 | 2300 | IRGD-23018 | IRGAHH-23018 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1233 | 1 | 2300 | IRGD-23019 | IRGD/OPT- 23019 | R-2315A~J | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 |  |  |  |  | d | F
1234 | 1 | 2300 | IRGD-23019 | IRGD/OPR- 23019 | R-2315A~J | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1862 | 0 | 2300 | IRGD-23019 | IRGAH-23019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1863 | 0 | 2300 | IRGD-23019 | IRGAHH-23019 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1235 | 1 | 2300 | IRGD-23020 | IRGD/P- 23020 | R-2301 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1865 | 0 | 2300 | IRGD-23020 | IRGAH-23020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1866 | 0 | 2300 | IRGD-23020 | IRGAHH-23020 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1236 | 1 | 2300 | IRGD-23021 | IRGD/P- 23021 | R-2302 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1868 | 0 | 2300 | IRGD-23021 | IRGAH-23021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1869 | 0 | 2300 | IRGD-23021 | IRGAHH-23021 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1237 | 1 | 2300 | IRGD-23022 | IRGD/P- 23022 | R-2303 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1871 | 0 | 2300 | IRGD-23022 | IRGAH-23022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1872 | 0 | 2300 | IRGD-23022 | IRGAHH-23022 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1238 | 1 | 2300 | IRGD-23023 | IRGD/P- 23023 | R-2304 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1874 | 0 | 2300 | IRGD-23023 | IRGAH-23023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1875 | 0 | 2300 | IRGD-23023 | IRGAHH-23023 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1239 | 1 | 2300 | IRGD-23024 | IRGD/P- 23024 | R-2305 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1877 | 0 | 2300 | IRGD-23024 | IRGAH-23024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1878 | 0 | 2300 | IRGD-23024 | IRGAHH-23024 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1240 | 1 | 2300 | IRGD-23025 | IRGD/P- 23025 | R-2306 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1880 | 0 | 2300 | IRGD-23025 | IRGAH-23025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1881 | 0 | 2300 | IRGD-23025 | IRGAHH-23025 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1241 | 1 | 2300 | IRGD-23026 | IRGD/P- 23026 | R-2307 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1883 | 0 | 2300 | IRGD-23026 | IRGAH-23026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1884 | 0 | 2300 | IRGD-23026 | IRGAHH-23026 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1242 | 1 | 2300 | IRGD-23027 | IRGD/P- 23027 | R-2308 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1886 | 0 | 2300 | IRGD-23027 | IRGAH-23027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1887 | 0 | 2300 | IRGD-23027 | IRGAHH-23027 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1243 | 1 | 2300 | IRGD-23028 | IRGD/P- 23028 | R-2309 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1889 | 0 | 2300 | IRGD-23028 | IRGAH-23028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1890 | 0 | 2300 | IRGD-23028 | IRGAHH-23028 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1244 | 1 | 2300 | IRGD-23029 | IRGD/P- 23029 | V-2325 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA80 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1892 | 0 | 2300 | IRGD-23029 | IRGAH-23029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1893 | 0 | 2300 | IRGD-23029 | IRGAHH-23029 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1245 | 1 | 2300 | IRGD-23030 | IRGD/P- 23030 | V-2318 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA80 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1895 | 0 | 2300 | IRGD-23030 | IRGAH-23030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1896 | 0 | 2300 | IRGD-23030 | IRGAHH-23030 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1246 | 1 | 2300 | IRGD-23031 | IRGD/P- 23031 | V-2320 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA80 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1898 | 0 | 2300 | IRGD-23031 | IRGAH-23031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1899 | 0 | 2300 | IRGD-23031 | IRGAHH-23031 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1247 | 1 | 2300 | IRGD-23032 | IRGD/P- 23032 | E-2315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1901 | 0 | 2300 | IRGD-23032 | IRGAH-23032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1902 | 0 | 2300 | IRGD-23032 | IRGAHH-23032 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1248 | 1 | 2300 | IRGD-23033 | IRGD/P- 23033 | R-2310 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1249 | 1 | 2300 | IRGD-23033 | IRGAH-23033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1250 | 1 | 2300 | IRGD-23033 | IRGAHH-23033 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1251 | 1 | 2300 | IRGD-23034 | IRGD/P- 23034 | R-2311 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1252 | 1 | 2300 | IRGD-23034 | IRGAH-23034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1253 | 1 | 2300 | IRGD-23034 | IRGAHH-23034 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1254 | 1 | 2300 | IRGD-23035 | IRGD/P- 23035 | R-2312 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1255 | 1 | 2300 | IRGD-23035 | IRGAH-23035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1256 | 1 | 2300 | IRGD-23035 | IRGAHH-23035 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1257 | 1 | 2300 | IRGD-23036 | IRGD/P- 23036 | R-2313 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1258 | 1 | 2300 | IRGD-23036 | IRGAH-23036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1259 | 1 | 2300 | IRGD-23036 | IRGAHH-23036 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1260 | 1 | 2300 | IRGD-23037 | IRGD/P- 23037 | R-2314 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1261 | 1 | 2300 | IRGD-23037 | IRGAH-23037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1262 | 1 | 2300 | IRGD-23037 | IRGAHH-23037 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1263 | 1 | 2300 | IRGD-23038 | IRGD/P- 23038 | V-2317 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1264 | 1 | 2300 | IRGD-23038 | IRGAH-23038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1265 | 1 | 2300 | IRGD-23038 | IRGAHH-23038 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1266 | 1 | 2300 | IRGD-23039 | IRGD/P- 23039 | V-2317S | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1267 | 1 | 2300 | IRGD-23039 | IRGAH-23039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1268 | 1 | 2300 | IRGD-23039 | IRGAHH-23039 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1269 | 1 | 2300 | IRGD-23040 | IRGD/P- 23040 | V-2319 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1270 | 1 | 2300 | IRGD-23040 | IRGAH-23040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1271 | 1 | 2300 | IRGD-23040 | IRGAHH-23040 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1272 | 1 | 2300 | IRGD-23041 | IRGD/P- 23041 | V-2315 | Point Type Gas Detector | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1273 | 1 | 2300 | IRGD-23041 | IRGAH-23041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1274 | 1 | 2300 | IRGD-23041 | IRGAHH-23041 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1275 | 1 | 2300 | IRGD-23042 | IRGD/OPT- 23042 | R-2315A~J | Open Path Type Gas Detector Transmitter | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 |  |  |  |  | d | F
1276 | 1 | 2300 | IRGD-23042 | IRGD/OPR- 23042 | R-2315A~J | Open Path Type Gas Detector Reciever | Flammable. Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1277 | 1 | 2300 | IRGD-23042 | IRGAH-23042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL |  | 25
1278 | 1 | 2300 | IRGD-23042 | IRGAHH-23042 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | %LFL | 50
1934 | 0 | 2300 | TGD-23001 | TGD-23001 | R-2301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1935 | 0 | 2300 | TGD-23001 | TGAH-23001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1936 | 0 | 2300 | TGD-23001 | TGAHH-23001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1279 | 3 | 0000 | TGD-23001 | TGA23001B | Toxic gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND13 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1280 | 2 | 0003 | TGD-23001 | TGA23001C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1939 | 0 | 2300 | TGD-23002 | TGD-23002 | R-2302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1940 | 0 | 2300 | TGD-23002 | TGAH-23002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1941 | 0 | 2300 | TGD-23002 | TGAHH-23002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1942 | 0 | 2300 | TGD-23003 | TGD-23003 | R-2303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1943 | 0 | 2300 | TGD-23003 | TGAH-23003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1944 | 0 | 2300 | TGD-23003 | TGAHH-23003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1945 | 0 | 2300 | TGD-23004 | TGD-23004 | R-2304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1946 | 0 | 2300 | TGD-23004 | TGAH-23004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1947 | 0 | 2300 | TGD-23004 | TGAHH-23004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1948 | 0 | 2300 | TGD-23005 | TGD-23005 | R-2305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1949 | 0 | 2300 | TGD-23005 | TGAH-23005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1950 | 0 | 2300 | TGD-23005 | TGAHH-23005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1951 | 0 | 2300 | TGD-23006 | TGD-23006 | R-2306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA71 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1952 | 0 | 2300 | TGD-23006 | TGAH-23006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1953 | 0 | 2300 | TGD-23006 | TGAHH-23006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1954 | 0 | 2300 | TGD-23007 | TGD-23007 | R-2307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1955 | 0 | 2300 | TGD-23007 | TGAH-23007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1956 | 0 | 2300 | TGD-23007 | TGAHH-23007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1957 | 0 | 2300 | TGD-23008 | TGD-23008 | R-2308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1958 | 0 | 2300 | TGD-23008 | TGAH-23008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1959 | 0 | 2300 | TGD-23008 | TGAHH-23008 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1960 | 0 | 2300 | TGD-23009 | TGD-23009 | R-2309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1961 | 0 | 2300 | TGD-23009 | TGAH-23009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1962 | 0 | 2300 | TGD-23009 | TGAHH-23009 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1963 | 0 | 2300 | TGD-23010 | TGD-23010 | R-2310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1964 | 0 | 2300 | TGD-23010 | TGAH-23010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1965 | 0 | 2300 | TGD-23010 | TGAHH-23010 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1966 | 0 | 2300 | TGD-23011 | TGD-23011 | R-2311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1967 | 0 | 2300 | TGD-23011 | TGAH-23011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1968 | 0 | 2300 | TGD-23011 | TGAHH-23011 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1969 | 0 | 2300 | TGD-23012 | TGD-23012 | R-2312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1970 | 0 | 2300 | TGD-23012 | TGAH-23012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1971 | 0 | 2300 | TGD-23012 | TGAHH-23012 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1972 | 0 | 2300 | TGD-23013 | TGD-23013 | R-2313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1973 | 0 | 2300 | TGD-23013 | TGAH-23013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1974 | 0 | 2300 | TGD-23013 | TGAHH-23013 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1975 | 0 | 2300 | TGD-23014 | TGD-23014 | R-2314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA73 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1976 | 0 | 2300 | TGD-23014 | TGAH-23014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1977 | 0 | 2300 | TGD-23014 | TGAHH-23014 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1978 | 0 | 2300 | TGD-23015 | TGD-23015 | V-2315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1979 | 0 | 2300 | TGD-23015 | TGAH-23015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1980 | 0 | 2300 | TGD-23015 | TGAHH-23015 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1981 | 0 | 2300 | TGD-23016 | TGD-23016 | V-2316 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1982 | 0 | 2300 | TGD-23016 | TGAH-23016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1983 | 0 | 2300 | TGD-23016 | TGAHH-23016 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1281 | 1 | 2300 | TGD-23017 | TGD-23017 | V-2317 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1985 | 0 | 2300 | TGD-23017 | TGAH-23017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1986 | 0 | 2300 | TGD-23017 | TGAHH-23017 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1282 | 1 | 2300 | TGD-23018 | TGD-23018 | V-2317S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1988 | 0 | 2300 | TGD-23018 | TGAH-23018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1989 | 0 | 2300 | TGD-23018 | TGAHH-23018 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1283 | 1 | 2300 | TGD-23019 | TGD-23019 | V-2319 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1991 | 0 | 2300 | TGD-23019 | TGAH-23019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1992 | 0 | 2300 | TGD-23019 | TGAHH-23019 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1284 | 1 | 2300 | TGD-23020 | TGD-23020 | R-2315A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1994 | 0 | 2300 | TGD-23020 | TGAH-23020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1995 | 0 | 2300 | TGD-23020 | TGAHH-23020 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1285 | 1 | 2300 | TGD-23021 | TGD-23021 | R-2315C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1997 | 0 | 2300 | TGD-23021 | TGAH-23021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1998 | 0 | 2300 | TGD-23021 | TGAHH-23021 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1286 | 1 | 2300 | TGD-23022 | TGD-23022 | R-2315E |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2000 | 0 | 2300 | TGD-23022 | TGAH-23022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2001 | 0 | 2300 | TGD-23022 | TGAHH-23022 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1287 | 1 | 2300 | TGD-23023 | TGD-23023 | R-2315G |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2003 | 0 | 2300 | TGD-23023 | TGAH-23023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2004 | 0 | 2300 | TGD-23023 | TGAHH-23023 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1288 | 1 | 2300 | TGD-23024 | TGD-23024 | R-2315I |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA74 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2006 | 0 | 2300 | TGD-23024 | TGAH-23024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2007 | 0 | 2300 | TGD-23024 | TGAHH-23024 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1289 | 1 | 2300 | TGD-23025 | TGD-23025 | V-2317 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2009 | 0 | 2300 | TGD-23025 | TGAH-23025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2010 | 0 | 2300 | TGD-23025 | TGAHH-23025 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1290 | 1 | 2300 | TGD-23026 | TGD-23026 | V-2317S |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2012 | 0 | 2300 | TGD-23026 | TGAH-23026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2013 | 0 | 2300 | TGD-23026 | TGAHH-23026 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1291 | 1 | 2300 | TGD-23027 | TGD-23027 | V-2319 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2015 | 0 | 2300 | TGD-23027 | TGAH-23027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2016 | 0 | 2300 | TGD-23027 | TGAHH-23027 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1292 | 1 | 2300 | TGD-23028 | TGD-23028 | V-2316 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2018 | 0 | 2300 | TGD-23028 | TGAH-23028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2019 | 0 | 2300 | TGD-23028 | TGAHH-23028 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1293 | 1 | 2300 | TGD-23029 | TGD-23029 | V-2315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2021 | 0 | 2300 | TGD-23029 | TGAH-23029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2022 | 0 | 2300 | TGD-23029 | TGAHH-23029 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1294 | 1 | 2300 | TGD-23030 | TGD-23030 | V-2301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2024 | 0 | 2300 | TGD-23030 | TGAH-23030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2025 | 0 | 2300 | TGD-23030 | TGAHH-23030 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1295 | 1 | 2300 | TGD-23031 | TGD-23031 | V-2302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2027 | 0 | 2300 | TGD-23031 | TGAH-23031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2028 | 0 | 2300 | TGD-23031 | TGAHH-23031 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1296 | 1 | 2300 | TGD-23032 | TGD-23032 | V-2303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2030 | 0 | 2300 | TGD-23032 | TGAH-23032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2031 | 0 | 2300 | TGD-23032 | TGAHH-23032 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1297 | 1 | 2300 | TGD-23033 | TGD-23033 | V-2304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2033 | 0 | 2300 | TGD-23033 | TGAH-23033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2034 | 0 | 2300 | TGD-23033 | TGAHH-23033 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1298 | 1 | 2300 | TGD-23034 | TGD-23034 | V-2305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2036 | 0 | 2300 | TGD-23034 | TGAH-23034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2037 | 0 | 2300 | TGD-23034 | TGAHH-23034 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1299 | 1 | 2300 | TGD-23035 | TGD-23035 | V-2306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2039 | 0 | 2300 | TGD-23035 | TGAH-23035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2040 | 0 | 2300 | TGD-23035 | TGAHH-23035 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1300 | 1 | 2300 | TGD-23036 | TGD-23036 | V-2307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2042 | 0 | 2300 | TGD-23036 | TGAH-23036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2043 | 0 | 2300 | TGD-23036 | TGAHH-23036 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1301 | 1 | 2300 | TGD-23037 | TGD-23037 | V-2308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2045 | 0 | 2300 | TGD-23037 | TGAH-23037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2046 | 0 | 2300 | TGD-23037 | TGAHH-23037 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1302 | 1 | 2300 | TGD-23038 | TGD-23038 | V-2309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2048 | 0 | 2300 | TGD-23038 | TGAH-23038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2049 | 0 | 2300 | TGD-23038 | TGAHH-23038 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1303 | 1 | 2300 | TGD-23039 | TGD-23039 | V-2310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2051 | 0 | 2300 | TGD-23039 | TGAH-23039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2052 | 0 | 2300 | TGD-23039 | TGAHH-23039 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1304 | 1 | 2300 | TGD-23040 | TGD-23040 | V-2311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2054 | 0 | 2300 | TGD-23040 | TGAH-23040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2055 | 0 | 2300 | TGD-23040 | TGAHH-23040 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1305 | 1 | 2300 | TGD-23041 | TGD-23041 | V-2312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2057 | 0 | 2300 | TGD-23041 | TGAH-23041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2058 | 0 | 2300 | TGD-23041 | TGAHH-23041 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1306 | 1 | 2300 | TGD-23042 | TGD-23042 | V-2313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2060 | 0 | 2300 | TGD-23042 | TGAH-23042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2061 | 0 | 2300 | TGD-23042 | TGAHH-23042 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1307 | 1 | 2300 | TGD-23043 | TGD-23043 | V-2314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2063 | 0 | 2300 | TGD-23043 | TGAH-23043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2064 | 0 | 2300 | TGD-23043 | TGAHH-23043 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1308 | 1 | 2300 | TGD-23044 | TGD-23044 | E-2315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1309 | 1 | 2300 | TGD-23044 | TGAH-23044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1310 | 1 | 2300 | TGD-23044 | TGAHH-23044 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1311 | 1 | 2300 | TGD-23045 | TGD-23045 | V-2318 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA80 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2069 | 0 | 2300 | TGD-23045 | TGAH-23045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2070 | 0 | 2300 | TGD-23045 | TGAHH-23045 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1312 | 1 | 2300 | TGD-23046 | TGD-23046 | V-2320 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA80 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2072 | 0 | 2300 | TGD-23046 | TGAH-23046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2073 | 0 | 2300 | TGD-23046 | TGAHH-23046 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
2074 | 0 | 2300 | TGD-23047 | TGD-23047 | V-2323 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA72 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2075 | 0 | 2300 | TGD-23047 | TGAH-23047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
2076 | 0 | 2300 | TGD-23047 | TGAHH-23047 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1313 | 1 | 2300 | TGD-23048 | TGD-23048 | E-2315 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA70 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1314 | 1 | 2300 | TGD-23048 | TGAH-23048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1315 | 1 | 2300 | TGD-23048 | TGAHH-23048 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1316 | 1 | 2300 | TGD-23049 | TGD-23049 | R-2301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1317 | 1 | 2300 | TGD-23049 | TGAH-23049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1318 | 1 | 2300 | TGD-23049 | TGAHH-23049 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1319 | 1 | 2300 | TGD-23050 | TGD-23050 | R-2302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA79 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1320 | 1 | 2300 | TGD-23050 | TGAH-23050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1321 | 1 | 2300 | TGD-23050 | TGAHH-23050 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1322 | 1 | 2300 | TGD-23063 | TGD-23063 | R-2315A |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 8 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1323 | 1 | 2300 | TGD-23063 | TGAH-23063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1324 | 1 | 2300 | TGD-23063 | TGAHH-23063 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1325 | 1 | 2300 | TGD-23064 | TGD-23064 | R-2315C |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1326 | 1 | 2300 | TGD-23064 | TGAH-23064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1327 | 1 | 2300 | TGD-23064 | TGAHH-23064 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1328 | 1 | 2300 | TGD-23065 | TGD-23065 | R-2315E |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 10 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1329 | 1 | 2300 | TGD-23065 | TGAH-23065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1330 | 1 | 2300 | TGD-23065 | TGAHH-23065 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1331 | 1 | 2300 | TGD-23066 | TGD-23066 | R-2315G |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 11 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1332 | 1 | 2300 | TGD-23066 | TGAH-23066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1333 | 1 | 2300 | TGD-23066 | TGAHH-23066 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1334 | 1 | 2300 | TGD-23067 | TGD-23067 | R-2315I |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA75 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1335 | 1 | 2300 | TGD-23067 | TGAH-23067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1336 | 1 | 2300 | TGD-23067 | TGAHH-23067 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1337 | 1 | 2300 | TGD-23059 | TGD-23059 | R-2311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1338 | 1 | 2300 | TGD-23059 | TGAH-23059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1339 | 1 | 2300 | TGD-23059 | TGAHH-23059 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1340 | 1 | 2300 | TGD-23060 | TGD-23060 | R-2312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1341 | 1 | 2300 | TGD-23060 | TGAH-23060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1342 | 1 | 2300 | TGD-23060 | TGAHH-23060 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1343 | 1 | 2300 | TGD-23061 | TGD-23061 | R-2313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1344 | 1 | 2300 | TGD-23061 | TGAH-23061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1345 | 1 | 2300 | TGD-23061 | TGAHH-23061 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1346 | 1 | 2300 | TGD-23062 | TGD-23062 | R-2314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA76 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1347 | 1 | 2300 | TGD-23062 | TGAH-23062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1348 | 1 | 2300 | TGD-23062 | TGAHH-23062 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1349 | 1 | 2300 | TGD-23051 | TGD-23051 | R-2303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1350 | 1 | 2300 | TGD-23051 | TGAH-23051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1351 | 1 | 2300 | TGD-23051 | TGAHH-23051 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1352 | 1 | 2300 | TGD-23052 | TGD-23052 | R-2304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1353 | 1 | 2300 | TGD-23052 | TGAH-23052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1354 | 1 | 2300 | TGD-23052 | TGAHH-23052 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1355 | 1 | 2300 | TGD-23053 | TGD-23053 | R-2305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1356 | 1 | 2300 | TGD-23053 | TGAH-23053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1357 | 1 | 2300 | TGD-23053 | TGAHH-23053 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1358 | 1 | 2300 | TGD-23054 | TGD-23054 | R-2306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA78 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1359 | 1 | 2300 | TGD-23054 | TGAH-23054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1360 | 1 | 2300 | TGD-23054 | TGAHH-23054 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1361 | 1 | 2300 | TGD-23055 | TGD-23055 | R-2307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1362 | 1 | 2300 | TGD-23055 | TGAH-23055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1363 | 1 | 2300 | TGD-23055 | TGAHH-23055 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1364 | 1 | 2300 | TGD-23056 | TGD-23056 | R-2308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1365 | 1 | 2300 | TGD-23056 | TGAH-23056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1366 | 1 | 2300 | TGD-23056 | TGAHH-23056 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1367 | 1 | 2300 | TGD-23057 | TGD-23057 | R-2309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 9 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1368 | 1 | 2300 | TGD-23057 | TGAH-23057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1369 | 1 | 2300 | TGD-23057 | TGAHH-23057 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1370 | 1 | 2300 | TGD-23058 | TGD-23058 | R-2310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA77 | 12 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1371 | 1 | 2300 | TGD-23058 | TGAH-23058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1372 | 1 | 2300 | TGD-23058 | TGAHH-23058 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1373 | 4 | 2300 | TGD-23068 | TGD-23068 | R-2301 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1374 | 4 | 2300 | TGD-23068 | TGAH-23068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1375 | 4 | 2300 | TGD-23068 | TGAHH-23068 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1376 | 4 | 2300 | TGD-23069 | TGD-23069 | R-2302 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1377 | 4 | 2300 | TGD-23069 | TGAH-23069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1378 | 4 | 2300 | TGD-23069 | TGAHH-23069 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1379 | 4 | 2300 | TGD-23070 | TGD-23070 | R-2303 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1380 | 4 | 2300 | TGD-23070 | TGAH-23070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1381 | 4 | 2300 | TGD-23070 | TGAHH-23070 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1382 | 4 | 2300 | TGD-23071 | TGD-23071 | R-2304 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1383 | 4 | 2300 | TGD-23071 | TGAH-23071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1384 | 4 | 2300 | TGD-23071 | TGAHH-23071 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1385 | 4 | 2300 | TGD-23072 | TGD-23072 | R-2305 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1386 | 4 | 2300 | TGD-23072 | TGAH-23072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1387 | 4 | 2300 | TGD-23072 | TGAHH-23072 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1388 | 4 | 2300 | TGD-23073 | TGD-23073 | R-2306 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1389 | 4 | 2300 | TGD-23073 | TGAH-23073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1390 | 4 | 2300 | TGD-23073 | TGAHH-23073 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1391 | 4 | 2300 | TGD-23074 | TGD-23074 | R-2307 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA83 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1392 | 4 | 2300 | TGD-23074 | TGAH-23074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1393 | 4 | 2300 | TGD-23074 | TGAHH-23074 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1394 | 4 | 2300 | TGD-23075 | TGD-23075 | R-2308 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1395 | 4 | 2300 | TGD-23075 | TGAH-23075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1396 | 4 | 2300 | TGD-23075 | TGAHH-23075 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1397 | 4 | 2300 | TGD-23076 | TGD-23076 | R-2309 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1398 | 4 | 2300 | TGD-23076 | TGAH-23076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1399 | 4 | 2300 | TGD-23076 | TGAHH-23076 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1400 | 4 | 2300 | TGD-23077 | TGD-23077 | R-2310 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1401 | 4 | 2300 | TGD-23077 | TGAH-23077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1402 | 4 | 2300 | TGD-23077 | TGAHH-23077 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1403 | 4 | 2300 | TGD-23078 | TGD-23078 | R-2311 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1404 | 4 | 2300 | TGD-23078 | TGAH-23078 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1405 | 4 | 2300 | TGD-23078 | TGAHH-23078 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1406 | 4 | 2300 | TGD-23079 | TGD-23079 | R-2312 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 5 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1407 | 4 | 2300 | TGD-23079 | TGAH-23079 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1408 | 4 | 2300 | TGD-23079 | TGAHH-23079 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1409 | 4 | 2300 | TGD-23080 | TGD-23080 | R-2313 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 6 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1410 | 4 | 2300 | TGD-23080 | TGAH-23080 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1411 | 4 | 2300 | TGD-23080 | TGAHH-23080 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1412 | 4 | 2300 | TGD-23081 | TGD-23081 | R-2314 |  | Toxic Gas (Open Area) | ESBR-HS-LYT-2302 | AIR | NIS | FGDS | CRR | d | F | 2300JNA84 | 7 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | PPM |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
1413 | 4 | 2300 | TGD-23081 | TGAH-23081 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM |  | 10
1414 | 4 | 2300 | TGD-23081 | TGAHH-23081 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | PPM | 50
1415 | 2 | 1600 | HD-16001 | HD-16001 | Y-2660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2138 | 0 | 1600 | HD-16001 | HA-16001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1416 | 3 | 0000 | HD-16001 | HA-16001B | Fire and Gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND16 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1417 | 1 | 0003 | HD-16001 | HA-16001C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1418 | 2 | 1600 | HD-16002 | HD-16002 | Y-2660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2142 | 0 | 1600 | HD-16002 | HA-16002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1419 | 2 | 1600 | HD-16003 | HD-16003 | Y-2660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2144 | 0 | 1600 | HD-16003 | HA-16003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1420 | 2 | 1600 | HD-16004 | HD-16004 | Y-1660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2146 | 0 | 1600 | HD-16004 | HA-16004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1421 | 2 | 1600 | HD-16005 | HD-16005 | Y-1660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2148 | 0 | 1600 | HD-16005 | HA-16005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Heat Alaram High | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1422 | 2 | 1600 | HD-16006 | HD-16006 | Y-1660 |  | Heat Detector (Open Area | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA71 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 2Wire, 0-20 mA acc. To mfr design
2150 | 0 | 1600 | HD-16006 | HA-16006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | High Alarm | ESBR-HS-CAF-0002 | [5 empty] | OWS | [10 empty] | C°/Min
1423 | 2 | 1600 | FD-16001 | FD-16001 | Y-2660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604 | AI | NIS | FGDS | FRR | d | F | 1600JNA70 | 1 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2152 | 0 | 1600 | FD-16001 | FAH-16001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1424 | 3 | 0000 | FD-16000 | FAH-16000B | Fire and Gas, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1425 | 3 | 0003 | FD-16000 | FA-16000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1426 | 2 | 1600 | FD-16002 | FD-16002 | Y-2660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604 | AI | NIS | FGDS | FRR | d | F | 1600JNA70 | 2 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2156 | 0 | 1600 | FD-16002 | FAH-16002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1427 | 2 | 1600 | FD-16003 | FD-16003 | Y-2660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604 | AI | NIS | FGDS | FRR | d | F | 1600JNA70 | 3 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2158 | 0 | 1600 | FD-16003 | FAH-16003 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1428 | 2 | 1600 | FD-16004 | FD-16004 | Y-1660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604 | AI | NIS | FGDS | FRR | d | F | 1600JNA70 | 4 | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2160 | 0 | 1600 | FD-16004 | FAH-16004 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1429 | 2 | 1600 | FD-16005 | FD-16005 | Y-1660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2162 | 0 | 1600 | FD-16005 | FAH-16005 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
1430 | 2 | 1600 | FD-16006 | FD-16006 | Y-1660 |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-1604(Rev.0) |  |  | FGDS | FRR | d | F | 1600JNA70 |  | 16-T-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2164 | 0 | 1600 | FD-16006 | FAH-16006 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0002 | [5 empty] | OWS
2165 | 0 | 1100 | DV-11001 | DV-11001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1431 | 1 | 1100 | DV-11001 | PT-11701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA80 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1432 | 1 | 1100 | DV-11001 | PT-11701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA80 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1101 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2168 | 0 | 1100 | DV-11001 | PI-11701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2169 | 0 | 1100 | DV-11001 | PI-11701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2170 | 0 | 1100 | DV-11001 | PI-11701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2171 | 0 | 1100 | DV-11001 | PI-11701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2172 | 0 | 1100 | DV-11001 | PI-11701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2173 | 0 | 1100 | DV-11001 | FO-11701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2174 | 0 | 1100 | DV-11001 | FO-11701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2175 | 0 | 1100 | DV-11001 | PSV11701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2176 | 0 | 1100 | DV-11001 | PCV-11701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1433 | 3 | 1100 | DV-11001 | HY-11701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1100JNS88 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
1434 | 3 | 1100 | DV-11001 | MR-11001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1100JNS88 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801
2179 | 0 | 1100 | DV-11001 | AG-11701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1435 | 3 | 0000 | DV-11001 | HS-11701B |  | HAND SWITCH(CONTROL ROOM) 11001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND11 | 1 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN
1436 | 4 | 0000 | DV-11001 | XS-11701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 11001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2181 | 0 | 1100 | DV-11001 | HS-11701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2182 | 0 | 1100 | DV-11001 | HSR-11701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1437 | 3 | 1100 | DV-11001 | PAH-11701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1438 | 3 | 1100 | DV-11001 | PAL-11701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2185 | 0 | 1100 | DV-11001 | UA-11701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1439 | 4 | 0000 | DV-11001 | PAL-11701AB |  | FUSIBLE LINK MELTED STATUS LAMP 11001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1440 | 4 | 0000 | DV-11001 | PAH-11701BB |  | DELUGE VALVE RELEASE STATUS LAMP 11001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1441 | 4 | 0003 | DV-11001 | PAL-11701AC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 11001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1442 | 4 | 0003 | DV-11001 | PAH-11701BC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 11001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2190 | 0 | 1100 | DV-11001 | FO-11500 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1101 | [5 empty] | F |  |  |  | 8"-FW-11001-1AAN-N | [15 empty] | Moved to Main Instrument Index
2191 | 0 | 1100 | DV-11002 | DV-11002 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, items are not finalised yet
1443 | 1 | 1100 | DV-11002 | PT-11702A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA81 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1444 | 1 | 1100 | DV-11002 | PT-11702B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA81 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2194 | 0 | 1100 | DV-11002 | PI-11702A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2195 | 0 | 1100 | DV-11002 | PI-11702B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2196 | 0 | 1100 | DV-11002 | PI-11702C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2197 | 0 | 1100 | DV-11002 | PI-11702D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2198 | 0 | 1100 | DV-11002 | PI-11702E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2199 | 0 | 1100 | DV-11002 | FO-11702 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2200 | 0 | 1100 | DV-11002 | FO-11702 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2201 | 0 | 1100 | DV-11002 | PSV11702 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2202 | 0 | 1100 | DV-11002 | PCV-11702 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1445 | 2 | 1100 | DV-11002 | HY-11702 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1100JNS82 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
1446 | 2 | 1100 | DV-11002 | MR-11002 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1100JNS82 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801
2205 | 0 | 1100 | DV-11002 | AG-11702 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1447 | 3 | 0000 | DV-11002 | HS-11702B |  | HAND SWITCH(CONTROL ROOM) 11002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND11 | 4 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1448 | 4 | 0000 | DV-11002 | XS-11702LB |  | HAND SWITCH LAMP (CONTROL ROOM) 11002 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2207 | 0 | 1100 | DV-11002 | HS-11702 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2208 | 0 | 1100 | DV-11002 | HSR-11702 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1449 | 3 | 1100 | DV-11002 | PAH-11702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1450 | 3 | 1100 | DV-11002 | PAL-11702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2211 | 0 | 1100 | DV-11002 | UA-11702 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1451 | 4 | 0000 | DV-11002 | PAL-11702BB |  | FUSIBLE LINK MELTED STATUS LAMP 11002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1452 | 4 | 0000 | DV-11002 | PAH-11702AB |  | DELUGE VALVE RELEASE STATUS LAMP 11002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1453 | 4 | 0003 | DV-11002 | PAL-11702BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 11002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1454 | 4 | 0003 | DV-11002 | PAH-11702AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 11002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2216 | 0 | 1100 | DV-11003 | DV-11003 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1455 | 1 | 1100 | DV-11003 | PT-11703A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA83 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1456 | 1 | 1100 | DV-11003 | PT-11703B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA83 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2219 | 0 | 1100 | DV-11003 | PI-11703A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2220 | 0 | 1100 | DV-11003 | PI-11703B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2221 | 0 | 1100 | DV-11003 | PI-11703C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2222 | 0 | 1100 | DV-11003 | PI-11703D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2223 | 0 | 1100 | DV-11003 | PI-11703E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2224 | 0 | 1100 | DV-11003 | FO-11703 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2225 | 0 | 1100 | DV-11003 | FO-11703 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2226 | 0 | 1100 | DV-11003 | PSV11703 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2227 | 0 | 1100 | DV-11003 | PCV-11703 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1457 | 2 | 1100 | DV-11003 | HY-11703 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1100JNS84 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
1458 | 2 | 1100 | DV-11003 | MR-11003 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1100JNS84 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801
2230 | 0 | 1100 | DV-11003 | AG-11703 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1459 | 3 | 0000 | DV-11003 | HS-11703B |  | HAND SWITCH(CONTROL ROOM) 11003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND11 | 7 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1460 | 4 | 0000 | DV-11003 | XS-11703LB |  | HAND SWITCH LAMP (CONTROL ROOM) 11003 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2232 | 0 | 1100 | DV-11003 | HS-11703 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2233 | 0 | 1100 | DV-11003 | HSR-11703 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1461 | 3 | 1100 | DV-11003 | PAH-11703 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1462 | 3 | 1100 | DV-11003 | PAL-11703 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2236 | 0 | 1100 | DV-11003 | UA-11703 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1463 | 4 | 0000 | DV-11003 | PAL-11703BB |  | FUSIBLE LINK MELTED STATUS LAMP 11003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1464 | 4 | 0000 | DV-11003 | PAH-11703AB |  | DELUGE VALVE RELEASE STATUS LAMP 11003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1465 | 4 | 0003 | DV-11003 | PAL-11703BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 11003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1466 | 4 | 0003 | DV-11003 | PAH-11703AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 11003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2241 | 0 | 1100 | DV-11003 | FO-11501 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1101 | [5 empty] | F |  |  |  | 6"-FW-11027-1AAN-N | [15 empty] | Moved to Main Instrument Index
2242 | 0 | 1100 | DV-11004 | DV-11004 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1467 | 1 | 1100 | DV-11004 | PT-11704A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA85 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1468 | 1 | 1100 | DV-11004 | PT-11704B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1100JNA85 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2245 | 0 | 1100 | DV-11004 | PI-11704A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2246 | 0 | 1100 | DV-11004 | PI-11704B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2247 | 0 | 1100 | DV-11004 | PI-11704C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2248 | 0 | 1100 | DV-11004 | PI-11704D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2249 | 0 | 1100 | DV-11004 | PI-11704E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2250 | 0 | 1100 | DV-11004 | FO-11704 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2251 | 0 | 1100 | DV-11004 | FO-11704 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2252 | 0 | 1100 | DV-11004 | PSV11704 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2253 | 0 | 1100 | DV-11004 | PCV-11704 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1469 | 2 | 1100 | DV-11004 | HY-11704 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1100JNS86 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 | ESBR-CI-DAS-0030
1470 | 2 | 1100 | DV-11004 | MR-11004 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1100JNS86 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801
2256 | 0 | 1100 | DV-11004 | AG-11704 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1471 | 3 | 0000 | DV-11004 | HS-11704B |  | HAND SWITCH(CONTROL ROOM) 11004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND11 | 10 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1472 | 4 | 0000 | DV-11004 | XS-11704LB |  | HAND SWITCH LAMP (CONTROL ROOM) 11004 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2258 | 0 | 1100 | DV-11004 | HS-11704 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2259 | 0 | 1100 | DV-11004 | HSR-11704 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1473 | 3 | 1100 | DV-11004 | PAH-11704 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1474 | 3 | 1100 | DV-11004 | PAL-11704 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2262 | 0 | 1100 | DV-11004 | UA-11704 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1475 | 3 | 0000 | DV-11004 | PAL-11704BB |  | FUSIBLE LINK MELTED STATUS LAMP 11004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1476 | 4 | 0000 | DV-11004 | PAH-11704AB |  | DELUGE VALVE RELEASE STATUS LAMP 11004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND11 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1477 | 4 | 0003 | DV-11004 | PAL-11704BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 11004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1478 | 4 | 0003 | DV-11004 | PAH-11704AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 11004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2267 | 0 | 1800 | DV-18001 | DV-18001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1479 | 1 | 1800 | DV-18001 | PT-18701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1800JNA82 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1480 | 1 | 1800 | DV-18001 | PT-18701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1800JNA82 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2270 | 0 | 1800 | DV-18001 | PI-18701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2271 | 0 | 1800 | DV-18001 | PI-18701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2272 | 0 | 1800 | DV-18001 | PI-18701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2273 | 0 | 1800 | DV-18001 | PI-18701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2274 | 0 | 1800 | DV-18001 | PI-18701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2275 | 0 | 1800 | DV-18001 | FO-18701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2276 | 0 | 1800 | DV-18001 | FO-18701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2277 | 0 | 1800 | DV-18001 | PSV18701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2278 | 0 | 1800 | DV-18001 | PCV-18701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1481 | 2 | 1800 | DV-18001 | HY-18701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1800JNS84 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
1482 | 2 | 1800 | DV-18001 | MR-18001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1800JNS84 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1802
2281 | 0 | 1800 | DV-18001 | AG-18701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2282 | 0 | 0000 | DV-18001 | HS-18701B |  | HAND SWITCH(CONTROL ROOM) 18001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND18 | 2 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
| 0 | 0000 | DV-18001 | XS-18701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 18001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2283 | 0 | 1800 | DV-18001 | HS-18701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2284 | 0 | 1800 | DV-18001 | HSR-18701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1483 | 3 | 1800 | DV-18001 | PAH-18701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1484 | 3 | 1800 | DV-18001 | PAL-18701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2287 | 0 | 1800 | DV-18001 | UA-18701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1485 | 4 | 0000 | DV-18001 | PAL-18701BB |  | FUSIBLE LINK MELTED STATUS LAMP 18001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1486 | 4 | 0000 | DV-18001 | PAH-18701AB |  | DELUGE VALVE RELEASE STATUS LAMP 18001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1487 | 4 | 0003 | DV-18001 | PAL-18701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 18001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1488 | 4 | 0003 | DV-18001 | PAH-18701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 18001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2292 | 0 | 1300 | DV-18001 | FO-18300 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1801 | [5 empty] | F |  |  |  | 6"-FW-18002-1AAN-N | [15 empty] | Moved to Main Instrument Index
2293 | 0 | 1800 | DV-18002 | DV-18002 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1489 | 1 | 1800 | DV-18002 | PT-18702A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1800JNA83 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1490 | 1 | 1800 | DV-18002 | PT-18702B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1800JNA83 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2296 | 0 | 1800 | DV-18002 | PI-18702A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2297 | 0 | 1800 | DV-18002 | PI-18702B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2298 | 0 | 1800 | DV-18002 | PI-18702C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2299 | 0 | 1800 | DV-18002 | PI-18702D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2300 | 0 | 1800 | DV-18002 | PI-18702E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2301 | 0 | 1800 | DV-18002 | FO-18702 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2302 | 0 | 1800 | DV-18002 | FO-18702 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2303 | 0 | 1800 | DV-18002 | PSV18702 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2304 | 0 | 1800 | DV-18002 | PCV-18702 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1491 | 2 | 1800 | DV-18002 | HY-18702 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1800JNS78 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1802 | ESBR-CI-DAS-0030
1492 | 2 | 1800 | DV-18002 | MR-18002 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1800JNS78 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1802
2307 | 0 | 1800 | DV-18002 | AG-18702 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2308 | 0 | 0000 | DV-18002 | HS-18702B |  | HAND SWITCH(CONTROL ROOM) 18002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND18 | 5 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1493 | 4 | 0000 | DV-18002 | XS-18702LB |  | HAND SWITCH LAMP (CONTROL ROOM) 18002 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2309 | 0 | 1800 | DV-18002 | HS-18702 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2310 | 0 | 1800 | DV-18002 | HSR-18702 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1494 | 3 | 1800 | DV-18002 | PAH-18702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1495 | 3 | 1800 | DV-18002 | PAL-18702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2313 | 0 | 1800 | DV-18002 | UA-18702 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1496 | 4 | 0000 | DV-18002 | PAL-18702BB |  | FUSIBLE LINK MELTED STATUS LAMP 18002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1497 | 4 | 0000 | DV-18002 | PAH-18702AB |  | DELUGE VALVE RELEASE STATUS LAMP 18002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1498 | 4 | 0003 | DV-18002 | PAL-18702BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 18002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1499 | 4 | 0003 | DV-18002 | PAH-18702AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 18002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2318 | 0 | 1300 | DV-13001 | DV-13001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1500 | 1 | 1300 | DV-13001 | PT-13701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1300JNA81 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1501 | 1 | 1300 | DV-13001 | PT-13701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1300JNA81 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2321 | 0 | 1300 | DV-13001 | PI-13701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2322 | 0 | 1300 | DV-13001 | PI-13701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2323 | 0 | 1300 | DV-13001 | PI-13701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2324 | 0 | 1300 | DV-13001 | PI-13701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2325 | 0 | 1300 | DV-13001 | PI-13701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2326 | 0 | 1300 | DV-13001 | FO-13701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2327 | 0 | 1300 | DV-13001 | FO-13701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2328 | 0 | 1300 | DV-13001 | PSV13701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2329 | 0 | 1300 | DV-13001 | PCV-13701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1502 | 2 | 1300 | DV-13001 | HY-13701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1300JNS82 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 | ESBR-CI-DAS-0030
1503 | 2 | 1300 | DV-13001 | MR-13001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1300JNS82 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301
2332 | 0 | 1300 | DV-13001 | AG-13701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1504 | 3 | 0000 | DV-13001 | HS-13701B |  | HAND SWITCH(CONTROL ROOM) 13001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND13 | 1 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1505 | 4 | 0000 | DV-13001 | XS-13701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 13001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2334 | 0 | 1300 | DV-13001 | HS-13701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2335 | 0 | 1300 | DV-13001 | HSR-13701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1506 | 3 | 1300 | DV-13001 | PAH-13701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1507 | 3 | 1300 | DV-13001 | PAL-13701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2338 | 0 | 1300 | DV-13001 | UA-13701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1508 | 4 | 0000 | DV-13001 | PAL-13701BB |  | FUSIBLE LINK MELTED STATUS LAMP 13001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1509 | 4 | 0000 | DV-13001 | PAH-13701AB |  | DELUGE VALVE RELEASE STATUS LAMP 13001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1510 | 4 | 0003 | DV-13001 | PAL-13701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 13001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1511 | 4 | 0003 | DV-13001 | PAH-13701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 13001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2343 | 0 | 1300 | DV-13001 | FO-13700 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-LYT-0016 | [5 empty] | F |  |  |  | 8"-FW-13001-1AAN-N | [15 empty] | Moved to Main Instrument Index
2344 | 0 | 2300 | DV-23001 | DV-23001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1512 | 1 | 2300 | DV-23001 | PT-23701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 2300JNA82 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1513 | 1 | 2300 | DV-23001 | PT-23701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 2300JNA82 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2347 | 0 | 2300 | DV-23001 | PI-23701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2348 | 0 | 2300 | DV-23001 | PI-23701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2349 | 0 | 2300 | DV-23001 | PI-23701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2350 | 0 | 2300 | DV-23001 | PI-23701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2351 | 0 | 2300 | DV-23001 | PI-23701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2352 | 0 | 2300 | DV-23001 | FO-23701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2353 | 0 | 2300 | DV-23001 | FO-23701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2354 | 0 | 2300 | DV-23001 | PSV23701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2355 | 0 | 2300 | DV-23001 | PCV-23701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1514 | 2 | 2300 | DV-23001 | HY-23701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 2300JNS83 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 | ESBR-CI-DAS-0030
1515 | 2 | 2300 | DV-23001 | MR-23001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 2300JNS83 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301
2358 | 0 | 2300 | DV-23001 | AG-23701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1516 | 3 | 0000 | DV-23001 | HS-23701B |  | HAND SWITCH(CONTROL ROOM) 23001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND13 | 4 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1517 | 4 | 0000 | DV-23001 | XS-23701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 23001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2360 | 0 | 2300 | DV-23001 | HS-23701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2361 | 0 | 2300 | DV-23001 | HSR-23701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1518 | 3 | 2300 | DV-23001 | PAH-23701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1519 | 3 | 2300 | DV-23001 | PAL-23701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2364 | 0 | 2300 | DV-23001 | UA-23701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1520 | 4 | 0000 | DV-23001 | PAH-23701AB |  | DELUGE VALVE RELEASE STATUS LAMP 23001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1521 | 4 | 0003 | DV-23001 | PAL-23701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 23001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1522 | 4 | 0003 | DV-23001 | PAH-23701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 23001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1523 | 4 | 0000 | DV-23001 | PAL-23701BB |  | FUSIBLE LINK MELTED STATUS LAMP 23001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Option
2369 | 0 | 2300 | DV-23001 | FO-23600 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-2301 | [5 empty] | F |  |  |  | 8"-FW-23001-1AAN-N | [15 empty] | Moved to Main Instrument Index
2370 | 0 | 1400 | DV-14001 | DV-14001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1524 | 1 | 1400 | DV-14001 | PT-14701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1400JNA90 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1525 | 1 | 1400 | DV-14001 | PT-14701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1400JNA90 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2373 | 0 | 1400 | DV-14001 | PI-14701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2374 | 0 | 1400 | DV-14001 | PI-14701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2375 | 0 | 1400 | DV-14001 | PI-14701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2376 | 0 | 1400 | DV-14001 | PI-14701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2377 | 0 | 1400 | DV-14001 | PI-14701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2378 | 0 | 1400 | DV-14001 | FO-14701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2379 | 0 | 1400 | DV-14001 | FO-14701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2380 | 0 | 1400 | DV-14001 | PSV14701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2381 | 0 | 1400 | DV-14001 | PCV-14701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1526 | 2 | 1400 | DV-14001 | HY-14701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1400JNS95 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 | ESBR-CI-DAS-0030
1527 | 2 | 1400 | DV-14001 | MR-14001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1400JNS95 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401
2384 | 0 | 1400 | DV-14001 | AG-14701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2385 | 0 | 0000 | DV-14001 | HS-14701B |  | HAND SWITCH(CONTROL ROOM) 14001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND14 | 11 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1528 | 4 | 0000 | DV-14001 | XS-14701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 14001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2386 | 0 | 1400 | DV-14001 | HS-14701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2387 | 0 | 1400 | DV-14001 | HSR-14701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1529 | 3 | 1400 | DV-14001 | PAH-14701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1530 | 3 | 1400 | DV-14001 | PAL-14701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2390 | 0 | 1400 | DV-14001 | UA-14701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1531 | 4 | 0000 | DV-14001 | PAL-14701BB |  | FUSIBLE LINK MELTED STATUS LAMP 14001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1532 | 4 | 0000 | DV-14001 | PAH-14701AB |  | DELUGE VALVE RELEASE STATUS LAMP 14001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1533 | 4 | 0003 | DV-14001 | PAL-14701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 14001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1534 | 4 | 0003 | DV-14001 | PAH-14701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 14001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2395 | 0 | 1400 | DV-14001 | FO-14500 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1401 | [5 empty] | F |  |  |  | 6"-FW-14002-1AAN-N | [15 empty] | Moved to Main Instrument Index
1535 | 4 | 1600 | DV-16030 | DV-16030 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1536 | 4 | 1600 | DV-16030 | PT-16701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1600JNA74 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1537 | 4 | 1600 | DV-16030 | PT-16701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1600JNA74 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1538 | 4 | 1600 | DV-16030 | PI-16701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
1539 | 4 | 1600 | DV-16030 | PI-16701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1540 | 4 | 1600 | DV-16030 | PI-16701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
1541 | 4 | 1600 | DV-16030 | PI-16701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
1542 | 4 | 1600 | DV-16030 | PI-16701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1543 | 4 | 1600 | DV-16030 | FO-16701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1544 | 4 | 1600 | DV-16030 | FO-16701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
1545 | 4 | 1600 | DV-16030 | PSV-16701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
1546 | 4 | 1600 | DV-16030 | PCV-16701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1547 | 4 | 1600 | DV-16030 | HY-16701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | FRR | d | F | 1600JNS75 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
1548 | 4 | 1600 | DV-16030 | MR-16030 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1600JNS75 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601
1549 | 4 | 1600 | DV-16030 | AG-16701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1550 | 4 | 0000 | DV-26030 | HS-26701B |  | HAND SWITCH(CONTROL ROOM) 26030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND19 | 2 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1551 | 4 | 0000 | DV-16030 | XS-16701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 16030 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1552 | 4 | 1600 | DV-16030 | HS-16701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1553 | 4 | 1600 | DV-16030 | HSR-16701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1554 | 4 | 1600 | DV-16030 | PAH-16701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1555 | 4 | 1600 | DV-16030 | PAL-16701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
1556 | 4 | 1600 | DV-16030 | UA-16701 |  |  | Cumilitive Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1557 | 4 | 0000 | DV-16030 | PAL-16701BB |  | FUSIBLE LINK MELTED STATUS LAMP 16030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1558 | 4 | 0000 | DV-16030 | PAH-16701AB |  | DELUGE VALVE RELEASE STATUS LAMP 16030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1559 | 4 | 0003 | DV-16030 | PAL-16701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 16030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1560 | 4 | 0003 | DV-16030 | PAH-16701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 16030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1561 | 4 | 0001 | DV-16030 | PAL-16701BF |  | FUSIBLE LINK MELTED STATUS LAMP OF AREA 16030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1562 | 4 | 0001 | DV-16030 | PAH-16701AF |  | DELUGE VALVE RELEASE STATUS LAMP 16030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1563 | 4 | 2600 | DV-26030 | DV-26030 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1564 | 4 | 2600 | DV-26030 | PT-26701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1600JNA76 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1565 | 4 | 2600 | DV-26030 | PT-26701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1600JNA76 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1566 | 4 | 2600 | DV-26030 | PI-26701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
1567 | 4 | 2600 | DV-26030 | PI-26701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1568 | 4 | 2600 | DV-26030 | PI-26701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
1569 | 4 | 2600 | DV-26030 | PI-26701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
1570 | 4 | 2600 | DV-26030 | PI-26701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1571 | 4 | 2600 | DV-26030 | FO-26701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1572 | 4 | 2600 | DV-26030 | FO-26701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
1573 | 4 | 2600 | DV-26030 | PSV-26701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
1574 | 4 | 2600 | DV-26030 | PCV-26701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1575 | 4 | 2600 | DV-26030 | HY-26701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | FRR | d | F | 1600JNS77 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 | ESBR-CI-DAS-0030
1576 | 4 | 2600 | DV-26030 | MR-26030 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1600JNS77 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601
1577 | 4 | 2600 | DV-26030 | AG-26701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1578 | 4 | 0000 | DV-36030 | HS-36701B |  | HAND SWITCH(CONTROL ROOM) 36030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND19 | 3 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1579 | 4 | 0000 | DV-26030 | XS-26701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 26030 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1580 | 4 | 2600 | DV-26030 | HS-26701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1581 | 4 | 2600 | DV-26030 | HSR-26701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1582 | 4 | 2600 | DV-26030 | PAH-26701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1583 | 4 | 2600 | DV-26030 | PAL-26701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
1584 | 4 | 2600 | DV-26030 | UA-26701 |  |  | Cumilitive Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1585 | 4 | 0000 | DV-26030 | PAL-26701BB |  | FUSIBLE LINK MELTED STATUS LAMP 26030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1586 | 4 | 0000 | DV-26030 | PAH-26701AB |  | DELUGE VALVE RELEASE STATUS LAMP 26030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1587 | 4 | 0003 | DV-26030 | PAL-26701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 26030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1588 | 4 | 0003 | DV-26030 | PAH-26701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 26030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1589 | 4 | 0001 | DV-26001 | PAL-26701BF |  | FUSIBLE LINK MELTED STATUS LAMP OF AREA 26030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1590 | 4 | 0001 | DV-26001 | PAH-26701AF |  | DELUGE VALVE RELEASE STATUS LAMP 26030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2446 | 0 | 1700 | DV-17001 | DV-17001 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1591 | 1 | 1700 | DV-17001 | PT-17701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA72 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1592 | 1 | 1700 | DV-17001 | PT-17701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA72 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2449 | 0 | 1700 | DV-17001 | PI-17701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2450 | 0 | 1700 | DV-17001 | PI-17701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2451 | 0 | 1700 | DV-17001 | PI-17701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2452 | 0 | 1700 | DV-17001 | PI-17701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2453 | 0 | 1700 | DV-17001 | PI-17701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2454 | 0 | 1700 | DV-17001 | FO-17701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2455 | 0 | 1700 | DV-17001 | FO-17701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2456 | 0 | 1700 | DV-17001 | PSV-17701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2457 | 0 | 1700 | DV-17001 | PCV-17701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1593 | 2 | 1700 | DV-17001 | HY-17701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1700JNS73 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
1594 | 2 | 1700 | DV-17001 | MR-17001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1700JNS73 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701
2460 | 0 | 1700 | DV-17001 | AG-17701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2461 | 0 | 0000 | DV-17001 | HS-17701B |  | HAND SWITCH(CONTROL ROOM) 17001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND17 | 13 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1595 | 4 | 0000 | DV-17001 | XS-17701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 17001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2462 | 0 | 1700 | DV-17001 | HS-17701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2463 | 0 | 1700 | DV-17001 | HSR-17701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1596 | 3 | 1700 | DV-17001 | PAH-17701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1597 | 3 | 1700 | DV-17001 | PAL-17701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2466 | 0 | 1700 | DV-17001 | UA-17701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1598 | 4 | 0000 | DV-17001 | PAL-17701BB |  | FUSIBLE LINK MELTED STATUS LAMP 17001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1599 | 4 | 0000 | DV-17001 | PAH-17701AB |  | DELUGE VALVE RELEASE STATUS LAMP 17001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1600 | 4 | 0003 | DV-17001 | PAL-17701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 17001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1601 | 4 | 0003 | DV-17001 | PAH-17701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 17001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2471 | 0 | 1700 | DV-17002 | DV-17002 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1602 | 1 | 1700 | DV-17002 | PT-17702A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA74 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1603 | 1 | 1700 | DV-17002 | PT-17702B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA74 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2474 | 0 | 1700 | DV-17002 | PI-17702A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
2475 | 0 | 1700 | DV-17002 | PI-17702B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2476 | 0 | 1700 | DV-17002 | PI-17702C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2477 | 0 | 1700 | DV-17002 | PI-17702D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2478 | 0 | 1700 | DV-17002 | PI-17702E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2479 | 0 | 1700 | DV-17002 | FO-17702 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2480 | 0 | 1700 | DV-17002 | FO-17702 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2481 | 0 | 1700 | DV-17002 | PSV-17702 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2482 | 0 | 1700 | DV-17002 | PCV-17702 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1604 | 2 | 1700 | DV-17002 | HY-17702 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1700JNS75 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
1605 | 2 | 1700 | DV-17002 | MR-17002 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1700JNS75 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701
2485 | 0 | 1700 | DV-17002 | AG-17702 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2486 | 0 | 0000 | DV-17002 | HS-17702B |  | HAND SWITCH(CONTROL ROOM) 17002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND17 | 11 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1606 | 4 | 0000 | DV-17002 | XS-17702LB |  | HAND SWITCH LAMP (CONTROL ROOM) 17002 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2487 | 0 | 1700 | DV-17002 | HS-17702 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2488 | 0 | 1700 | DV-17002 | HSR-17702 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1607 | 3 | 1700 | DV-17002 | PAH-17702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1608 | 3 | 1700 | DV-17002 | PAL-17702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2491 | 0 | 1700 | DV-17002 | UA-17702 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1609 | 4 | 0000 | DV-17002 | PAL-17702BB |  | FUSIBLE LINK MELTED STATUS LAMP 17002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1610 | 4 | 0000 | DV-17002 | PAH-17702AB |  | DELUGE VALVE RELEASE STATUS LAMP 17002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1611 | 4 | 0003 | DV-17002 | PAL-17702BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 17002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1612 | 4 | 0003 | DV-17002 | PAH-17702AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 17002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2496 | 0 | 1700 | DV-17003 | DV-17003 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1613 | 1 | 1700 | DV-17003 | PT-17703A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA76 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1614 | 1 | 1700 | DV-17003 | PT-17703B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1700JNA76 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2499 | 0 | 1700 | DV-17003 | PI-17703A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2500 | 0 | 1700 | DV-17003 | PI-17703B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
2501 | 0 | 1700 | DV-17003 | PI-17703C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
2502 | 0 | 1700 | DV-17003 | PI-17703D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
2503 | 0 | 1700 | DV-17003 | PI-17703E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2504 | 0 | 1700 | DV-17003 | FO-17703 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
2505 | 0 | 1700 | DV-17003 | FO-17703 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
2506 | 0 | 1700 | DV-17003 | PSV17703 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
2507 | 0 | 1700 | DV-17003 | PCV-17703 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1615 | 2 | 1700 | DV-17003 | HY-17703 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1700JNS77 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701 | ESBR-CI-DAS-0030
1616 | 2 | 1700 | DV-17003 | MR-17003 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1700JNS77 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701
2510 | 0 | 1700 | DV-17003 | AG-17703 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
2511 | 0 | 0000 | DV-17003 | HS-17703B |  | HAND SWITCH(CONTROL ROOM) 17003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND17 | 12 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1617 | 4 | 0000 | DV-17003 | XS-17703LB |  | HAND SWITCH LAMP (CONTROL ROOM) 17003 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2512 | 0 | 1700 | DV-17003 | HS-17703 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2513 | 0 | 1700 | DV-17003 | HSR-17703 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1618 | 3 | 1700 | DV-17003 | PAH-17703 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1619 | 3 | 1700 | DV-17003 | PAL-17703 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2516 | 0 | 1700 | DV-17003 | UA-17703 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
2517 | 0 | 0000 | DV-17003 | PAL-17703B |  | FUSIBLE LINK MELTED STATUS LAMP 17003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2518 | 0 | 0000 | DV-17003 | PAH-17703B |  | DELUGE VALVE RELEASE STATUS LAMP 17003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1620 | 1 | 0003 | DV-17003 | PAL-17703C | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 17003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1621 | 1 | 0003 | DV-17003 | PAH-17703C | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 17003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1622 | 3 | 1900 | DV-19001 | DV-19001 | Typical B |  | Deluge Valve | ESBR-HS-PID-1912 | [13 empty] | OPEN
1623 | 3 | 1900 | DV-19001 | PT-19701 |  |  | Pressure Transmitter Water line | ESBR-HS-PID-1913 | AIR | NIS | FGDS | CRR | d | F | 1900JNA71 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | %
1624 | 3 | 1900 | DV-19001 | PI-19701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1625 | 3 | 1900 | DV-19001 | PI-19701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1626 | 3 | 1900 | DV-19001 | PI-19701C |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1627 | 3 | 1900 | DV-19001 | FO-19701 |  |  | Orifice Plate water | ESBR-HS-PID-1912
1628 | 3 | 1900 | DV-19001 | AG-19701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912
1629 | 3 | 1900 | DV-19001 | HY-19701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | 1900JNS75 | 1 | 01-P-2.50-01-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
1630 | 4 | 1900 | DV-19001 | MR-19001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1900JNS75 | 2 | 01-P-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1631 | 3 | 0000 | DV-19001 | HS-19701B |  | HAND SWITCH(CONTROL ROOM) 19001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND17 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1632 | 4 | 0000 | DV-19001 | XS-19701LB |  | HAND SWITCH LAMP (CONTROL ROOM) 19001 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1633 | 3 | 0000 | DV-19001 | PAH-19701B |  | DELUGE VALVE RELEASE STATUS LAMP 19001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 15 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1634 | 3 | 0003 | DV-19001 | PAH-19701C |  | DELUGE VALVE RELEASE STATUS LAMP 19001 | Signal to GFAP In Fire station | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1635 | 3 | 1900 | DV-19001 | PAH-19701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1636 | 3 | 1900 | DV-19001 | HS-19701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1637 | 3 | 1900 | DV-19001 | HSR-19701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1638 | 3 | 1900 | DV-19001 | UA-19701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1639 | 4 | 1900 | DV-19002 | DV-19002 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1640 | 4 | 1900 | DV-19002 | PT-19702A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1900JNA72 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1641 | 4 | 1900 | DV-19002 | PT-19702B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 1900JNA72 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1642 | 4 | 1900 | DV-19002 | PI-19702A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
1643 | 4 | 1900 | DV-19002 | PI-19702B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1644 | 4 | 1900 | DV-19002 | PI-19702C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
1645 | 4 | 1900 | DV-19002 | PI-19702D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
1646 | 4 | 1900 | DV-19002 | PI-19702E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1647 | 4 | 1900 | DV-19002 | FO-19702 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1648 | 4 | 1900 | DV-19002 | FO-19702 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
1649 | 4 | 1900 | DV-19002 | PSV-19702 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
1650 | 4 | 1900 | DV-19002 | PCV-19702 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1651 | 4 | 1900 | DV-19002 | HY-19702 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | FRR | d | F | 1900JNS77 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
1652 | 4 | 1900 | DV-19002 | MR-36030 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 1900JNS77 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601
1653 | 4 | 1900 | DV-19002 | AG-19702 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1654 | 4 | 0000 | DV-19002 | HS-19702B |  | HAND SWITCH(CONTROL ROOM) 19002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP |  | 3 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1655 | 4 | 0000 | DV-19002 | XS-19702LB |  | HAND SWITCH LAMP (CONTROL ROOM)19002 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP | 1000CND19 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1656 | 4 | 1900 | DV-19002 | HS-19702 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1657 | 4 | 1900 | DV-19002 | HSR-19702 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1658 | 4 | 1900 | DV-19002 | PAH-19702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1659 | 4 | 1900 | DV-19002 | PAL-19702 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
1660 | 4 | 1900 | DV-19002 | UA-19702 |  |  | Cumilitive Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1661 | 4 | 0000 | DV-19002 | PAL-19702BB |  | FUSIBLE LINK MELTED STATUS LAMP 19002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1662 | 4 | 0000 | DV-19002 | PAH-19702AB |  | DELUGE VALVE RELEASE STATUS LAMP 19002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1663 | 4 | 0003 | DV-19002 | PAL-19702BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 19002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1664 | 4 | 0003 | DV-19002 | PAH-19702AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 19002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1665 | 4 | 3600 | DV-36030 | DV-36030 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1666 | 4 | 3600 | DV-36030 | PT-36701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 3600JNA73 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1667 | 4 | 3600 | DV-36030 | PT-36701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 3600JNA73 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1668 | 4 | 3600 | DV-36030 | PI-36701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
1669 | 4 | 3600 | DV-36030 | PI-36701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1670 | 4 | 3600 | DV-36030 | PI-36701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
1671 | 4 | 3600 | DV-36030 | PI-36701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
1672 | 4 | 3600 | DV-36030 | PI-36701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1673 | 4 | 3600 | DV-36030 | FO-36701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1674 | 4 | 3600 | DV-36030 | FO-36701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
1675 | 4 | 3600 | DV-36030 | PSV-36701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
1676 | 4 | 3600 | DV-36030 | PCV-36701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1677 | 4 | 3600 | DV-36030 | HY-36701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | FRR | d | F | 3600JNS74 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
1678 | 4 | 3600 | DV-36030 | MR-36030 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 3600JNS74 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601
1679 | 4 | 3600 | DV-36030 | AG-36701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1680 | 4 | 0000 | DV-46030 | HS-46701B |  | HAND SWITCH(CONTROL ROOM) 46030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND19 | 9 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1681 | 4 | 0000 | DV-36030 | XS-36701LB |  | HAND SWITCH LAMP (CONTROL ROOM)36030 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1682 | 4 | 3600 | DV-36030 | HS-36701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1683 | 4 | 3600 | DV-36030 | HSR-36701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1684 | 4 | 3600 | DV-36030 | PAH-36701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1685 | 4 | 3600 | DV-36030 | PAL-36701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
1686 | 4 | 3600 | DV-36030 | UA-36701 |  |  | Cumilitive Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1687 | 4 | 0000 | DV-36030 | PAL-36701BB |  | FUSIBLE LINK MELTED STATUS LAMP 36030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1688 | 4 | 0000 | DV-36030 | PAH-36701AB |  | DELUGE VALVE RELEASE STATUS LAMP 36030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1689 | 4 | 0003 | DV-36030 | PAL-36701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 36030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1690 | 4 | 0003 | DV-36030 | PAH-36701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 36030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1691 | 4 | 0001 | DV-36030 | PAL-36701BF |  | FUSIBLE LINK MELTED STATUS LAMP OF AREA 36030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1692 | 4 | 0001 | DV-36030 | PAH-36701AF |  | DELUGE VALVE RELEASE STATUS LAMP 36030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1693 | 4 | 4600 | DV-46030 | DV-46030 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1694 | 4 | 4600 | DV-46030 | PT-46701A | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 3600JNA75 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1695 | 4 | 4600 | DV-46030 | PT-46701B | The JBs are usually supplied by package vendor |  | Pressure Transmitter Air Line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | FRR | d | F | 3600JNA75 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1696 | 4 | 4600 | DV-46030 | PI-46701A |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F | [19 empty] | Data will be modified based on vendor data
1697 | 4 | 4600 | DV-46030 | PI-46701B |  |  | Pressure Indicator (water line) | ESBR-HS-PID-1912 | [5 empty] | F
1698 | 4 | 4600 | DV-46030 | PI-46701C |  |  | Pressure Indicator related to regualting valve | ESBR-HS-PID-1912 | [5 empty] | F
1699 | 4 | 4600 | DV-46030 | PI-46701D |  |  | Pressure Indicator related to Pilot | ESBR-HS-PID-1912 | [5 empty] | F
1700 | 4 | 4600 | DV-46030 | PI-46701E |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1701 | 4 | 4600 | DV-46030 | FO-46701 A |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1702 | 4 | 4600 | DV-46030 | FO-46701 B |  |  | Orifice Plate Air | ESBR-HS-PID-1912 | [5 empty] | F
1703 | 4 | 4600 | DV-46030 | PSV-46701 |  |  | Pressure Safety Valve | ESBR-HS-PID-1912 | [5 empty] | F
1704 | 4 | 4600 | DV-46030 | PCV-46701 |  |  | Regulating valve | ESBR-HS-PID-1912 | [5 empty] | F
1705 | 4 | 4600 | DV-46030 | HY-46701 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | FRR | d | F | 3600JNS76 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601 | ESBR-CI-DAS-0030
1706 | 4 | 4600 | DV-46030 | MR-46002 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 |  | NIS |  |  | d | F | 3600JNS76 | 2 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-3601
1707 | 4 | 4600 | DV-46030 | AG-46701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1708 | 3 | 0000 | MCP-21000 | MCP-21000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 2100 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND19 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1709 | 4 | 0000 | DV-46030 | XS-46701LB |  | HAND SWITCH LAMP (CONTROL ROOM)46030 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1710 | 4 | 4600 | DV-46030 | HS-46701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
1711 | 4 | 4600 | DV-46030 | HSR-46701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
1712 | 4 | 4600 | DV-46030 | PAH-46701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1713 | 4 | 4600 | DV-46030 | PAL-46701 | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
1714 | 4 | 4600 | DV-46030 | UA-46701 |  |  | Cumilitive Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1715 | 4 | 0000 | DV-46030 | PAL-46701B |  | FUSIBLE LINK MELTED STATUS LAMP 46030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1716 | 4 | 0000 | DV-46030 | PAH-46701AB |  | DELUGE VALVE RELEASE STATUS LAMP 46030 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1717 | 4 | 0003 | DV-46030 | PAL-46701BC | Signal connection through remote I/O | FUSIBLE LINK MELTED STATUS LAMP OF AREA 46030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1718 | 4 | 0003 | DV-46030 | PAH-46701AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 46030 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1719 | 4 | 0001 | DV-46030 | PAL-46701BF |  | FUSIBLE LINK MELTED STATUS LAMP OF AREA 46030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1720 | 4 | 0001 | DV-46030 | PAH-46701AF |  | DELUGE VALVE RELEASE STATUS LAMP 46030 | Signal to Matrix Panel Central Control Room (FCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | FRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2587 | 0 | 1200 | DV-12001 | DV-12001 | Typical C |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1721 | 1 | 1200 | DV-12001 | PT-12701 | The JBs are usually supplied by package vendor |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1200JNA72 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2589 | 0 | 1200 | DV-12001 | PI-12701A |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2590 | 0 | 1200 | DV-12001 | PI-12701B |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1722 | 3 | 1200 | DV-12001 | PI-12701C |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2592 | 0 | 1200 | DV-12001 | FO-12701 |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1723 | 2 | 1200 | DV-12001 | MR-12001 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR | d | F | 1200JND73 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2594 | 0 | 1200 | DV-12001 | AG-12701 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1724 | 3 | 0000 | DV-12001 | HS-12701B |  | HAND SWITCH(CONTROL ROOM) 12001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND28 | 7 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1725 | 4 | 0000 | DV-12001 | XS-12701LB |  | HAND SWITCH LAMP (CONTROL ROOM)12701 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2596 | 0 | 1200 | DV-12001 | HS-12701 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2597 | 0 | 1200 | DV-12001 | HSR-12701 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
2598 | 0 | 1200 | DV-12001 | PAH-12701A | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
2599 | 0 | 1200 | DV-12001 | PAL-12701A | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2600 | 0 | 1200 | DV-12001 | UA-12701 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1726 | 2 | 0000 | DV-12001 | PAL-12701B |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND12 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1727 | 3 | 0000 | DV-12001 | PAH-12701B |  | DELUGE VALVE RELEASE STATUS LAMP 12001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1728 | 1 | 0003 | DV-12001 | PAL-12701C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  |  | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1729 | 1 | 0003 | DV-12001 | PAH-12701C | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 12001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2605 | 0 | 1200 | DV-12001 | FO-12400 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1201 | [5 empty] | F |  |  |  | 4"-FW-12013-1AAN-N | [15 empty] | Moved to Main Instrument Index
2606 | 0 | 1200 | DV-12002 | DV-12002 | Typical A |  | Deluge Valve | ESBR-HS-PID-1912 | [5 empty] | F | [7 empty] | OPEN | [11 empty] | Package, Signals are not finalised yet
1730 | 1 | 1200 | DV-12002 | PT-12702A |  |  | Pressure Transmitter Water line | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1200JNA74 | 1 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
1731 | 1 | 1200 | DV-12002 | PT-12702B |  |  | Pressure Transmitter Water Air | ESBR-HS-PID-1912 | AIR | NIS | FGDS | CRR | d | F | 1200JNA74 | 2 | 04-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc |  |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 2-Wire 4-20 mA
2608 | 0 | 1200 | DV-12002 | PI-12702A |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1732 | 4 | 1200 | DV-12002 | PI-12702B |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
1733 | 3 | 1200 | DV-12002 | PI-12702C |  |  | Pressure Indicator | ESBR-HS-PID-1912 | [5 empty] | F
2611 | 0 | 1200 | DV-12002 | FO-12702 |  |  | Orifice Plate water | ESBR-HS-PID-1912 | [5 empty] | F
1734 | 4 | 1200 | DV-12002 | MR-12002 |  | The JBs are usually supplied by package vendor | Manual Release | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR | d | F | 1200JNS75 | 1 | 01-P-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/43 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2613 | 0 | 1200 | DV-12002 | AG-12702 |  |  | Water Alarm GONG | ESBR-HS-PID-1912 | [5 empty] | F
1735 | 3 | 0000 | DV-12002 | HS-12702B |  | HAND SWITCH(CONTROL ROOM) 12002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | CRR |  | MP | 1000CND28 | 9 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
1736 | 4 | 0000 | DV-12002 | XS-12702LB |  | HAND SWITCH LAMP (CONTROL ROOM)12702 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-PID-1912 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
1737 | 4 | 1200 | DV-12002 | HY-12702 |  | The JBs are usually supplied by package vendor | Controller for solenoid | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR |  | F | 1200JNS75 | 2 | 01-P-2.50-01-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
2615 | 0 | 1200 | DV-12002 | HS-12702 |  | Software switch | Handswitch Remote | ESBR-HS-PID-1912 | [5 empty] | OWS
2616 | 0 | 1200 | DV-12002 | HSR-12702 |  | Software reset switch | Handswitch reset | ESBR-HS-PID-1912 | [5 empty] | OWS
2617 | 0 | 1200 | DV-12002 | PAH-12702A | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm High (water) | ESBR-HS-PID-1912 | [5 empty] | OWS
1738 | 4 | 1200 | DV-12002 | PAL-12702B | AUDIBLE ALARM (CONTINUOUS ) | (RED FLASHING LIGHT) | Pressure Alarm Low (Air) | ESBR-HS-PID-1912 | [5 empty] | OWS
2619 | 0 | 1200 | DV-12002 | UA-12702 |  |  | Cumulative Alarm (Control Room) | ESBR-HS-PID-1912 | [5 empty] | OWS
1739 | 4 | 0000 | DV-12002 | PAL-12702BB |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND12 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1740 | 4 | 0000 | DV-12002 | PAH-12702AB |  | DELUGE VALVE RELEASE STATUS LAMP 12002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1741 | 4 | 0003 | DV-12002 | PAL-12702BC | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  |  | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1742 | 4 | 0003 | DV-12002 | PAH-12702AC | Signal connection through remote I/O | DELUGE VALVE RELEASE STATUS LAMP 12002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2624 | 0 | 1200 | DV-12002 | FO-12401 | Fire water Ring Main |  | Orifice Plate Main Line | ESBR-HS-PID-1201 | [5 empty] | F |  |  |  | 4"-FW-12002-1AAN-N | [15 empty] | Moved to Main Instrument Index
1743 | 1 | 1100 | SH-11001 | FSH-11751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-11001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 |  |  |  | Replaced with 1100JND87
2626 | 0 | 1100 | SH-11001 | FAH-11751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2627 | 0 | 1100 | SH-11001 | FO-11751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1744 | 4 | 1100 | SH-11001 | UK-11751 |  |  | Siren located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-11001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1745 | 4 | 1100 | SH-11001 | UL-11751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-11001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1746 | 3 | 0000 | SH-11001 | SHA-11001B |  | SHOWER/EYEWASH ACTIVATION ALARM 11001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1747 | 1 | 0003 | SH-11001 | SHA-11001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 11001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1748 | 4 | 1100 | SH-11002 | FSH-11752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-11002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1801 |  |  |  | Replaced with 1100JND87
1749 | 4 | 1100 | SH-11002 | FAH-11752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1750 | 4 | 1100 | SH-11002 | FO-11752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1751 | 4 | 1100 | SH-11002 | UK-11752 |  |  | Siren located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-11002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1752 | 4 | 1100 | SH-11002 | UL-11752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-11002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1753 | 3 | 0000 | SH-11002 | SHA-11002B |  | SHOWER/EYEWASH ACTIVATION ALARM 11002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND28 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1754 | 1 | 0003 | SH-11002 | SHA-11002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 11002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1755 | 4 | 1800 | SH-18001 | FSH-18752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-18001 |  | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1802
1756 | 4 | 1800 | SH-18001 | FAH-18752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1757 | 4 | 1800 | SH-18001 | FO-18752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1758 | 4 | 1800 | SH-18001 | UK-11752 |  |  | Siren located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-18001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1759 | 4 | 1800 | SH-18001 | UL-11752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-18001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2638 | 0 | 0000 | SH-18001 | SHA-18001B |  | SHOWER/EYEWASH ACTIVATION ALARM 18001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1760 | 1 | 0003 | SH-18001 | SHA-18002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 18001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1761 | 4 | 1200 | SH-12001 | FSH-12751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1762 | 4 | 1200 | SH-12001 | FAH-12751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1763 | 4 | 1200 | SH-12001 | FO-12751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1764 | 4 | 1200 | SH-12001 | UK-12751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1765 | 4 | 1200 | SH-12001 | UL-12751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1766 | 3 | 0000 | SH-12001 | SHA-12001B |  | SHOWER/EYEWASH ACTIVATION ALARM 12001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1767 | 1 | 0003 | SH-12001 | SHA-12001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1768 | 4 | 1200 | SH-12002 | FSH-12752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1769 | 4 | 1200 | SH-12002 | FAH-12752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1770 | 4 | 1200 | SH-12002 | FO-12752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1771 | 4 | 1200 | SH-12002 | UK-12752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1772 | 4 | 1200 | SH-12002 | UL-12752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1773 | 3 | 0000 | SH-12002 | SHA-12002B |  | SHOWER/EYEWASH ACTIVATION ALARM 12002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1774 | 1 | 0003 | SH-12002 | SHA-12002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1775 | 4 | 1200 | SH-12003 | FSH-12753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1776 | 4 | 1200 | SH-12003 | FAH-12753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1777 | 4 | 1200 | SH-12003 | FO-12753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1778 | 4 | 1200 | SH-12003 | UK-12753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1779 | 4 | 1200 | SH-12003 | UL-12753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1780 | 3 | 0000 | SH-12003 | SHA-12003B |  | SHOWER/EYEWASH ACTIVATION ALARM 12003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1781 | 1 | 0003 | SH-12003 | SHA-12003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1782 | 4 | 1200 | SH-12004 | FSH-12754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1783 | 4 | 1200 | SH-12004 | FAH-12754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1784 | 4 | 1200 | SH-12004 | FO-12754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1785 | 4 | 1200 | SH-12004 | UK-12754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1786 | 4 | 1200 | SH-12004 | UL-12754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1787 | 3 | 0000 | SH-12004 | SHA-12004B |  | SHOWER/EYEWASH ACTIVATION ALARM 12004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1788 | 1 | 0003 | SH-12004 | SHA-12004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1789 | 4 | 1200 | SH-12005 | FSH-12755 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12005 | 5 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1790 | 4 | 1200 | SH-12005 | FAH-12755 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1791 | 4 | 1200 | SH-12005 | FO-12755 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1792 | 4 | 1200 | SH-12005 | UK-12755 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12005 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1793 | 4 | 1200 | SH-12005 | UL-12755 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12005 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1794 | 3 | 0000 | SH-12005 | SHA-12005B |  | SHOWER/EYEWASH ACTIVATION ALARM 12005 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1795 | 1 | 0003 | SH-12005 | SHA-12005C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12005 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1796 | 4 | 1200 | SH-12006 | FSH-12756 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12006 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1797 | 4 | 1200 | SH-12006 | FAH-12756 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1798 | 4 | 1200 | SH-12006 | FO-12756 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1799 | 4 | 1200 | SH-12006 | UK-12756 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12006 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1800 | 4 | 1200 | SH-12006 | UL-12756 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12006 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1801 | 3 | 0000 | SH-12006 | SHA-12006B |  | SHOWER/EYEWASH ACTIVATION ALARM 12006 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1802 | 1 | 0003 | SH-12006 | SHA-12006C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12006 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1803 | 4 | 1200 | SH-12007 | FSH-12757 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12007 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1804 | 4 | 1200 | SH-12007 | FAH-12757 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1805 | 4 | 1200 | SH-12007 | FO-12757 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1806 | 4 | 1200 | SH-12007 | UK-12757 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12007 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1807 | 4 | 1200 | SH-12007 | UL-12757 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12007 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1808 | 3 | 0000 | SH-12007 | SHA-12007B |  | SHOWER/EYEWASH ACTIVATION ALARM 12007 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1809 | 1 | 0003 | SH-12007 | SHA-12007C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12007 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1810 | 4 | 1200 | SH-12008 | FSH-12758 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12008 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1811 | 4 | 1200 | SH-12008 | FAH-12758 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1812 | 4 | 1200 | SH-12008 | FO-12758 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1813 | 4 | 1200 | SH-12008 | UK-12758 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12008 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1814 | 4 | 1200 | SH-12008 | UL-12758 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12008 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1815 | 3 | 0000 | SH-12008 | SHA-12008B |  | SHOWER/EYEWASH ACTIVATION ALARM 12008 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1816 | 1 | 0003 | SH-12008 | SHA-12008C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12008 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1817 | 4 | 1200 | SH-12009 | FSH-12759 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12009 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1818 | 4 | 1200 | SH-12009 | FAH-12759 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1819 | 4 | 1200 | SH-12009 | FO-12759 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1820 | 4 | 1200 | SH-12009 | UK-12759 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12009 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1821 | 4 | 1200 | SH-12009 | UL-12759 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12009 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1822 | 3 | 0000 | SH-12009 | SHA-12009B |  | SHOWER/EYEWASH ACTIVATION ALARM 12009 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1823 | 1 | 0003 | SH-12009 | SHA-12009C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12009 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1824 | 4 | 1200 | SH-12010 | FSH-12760 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12010 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1825 | 4 | 1200 | SH-12010 | FAH-12760 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1826 | 4 | 1200 | SH-12010 | FO-12760 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1827 | 4 | 1200 | SH-12010 | UK-12760 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12010 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1828 | 4 | 1200 | SH-12010 | UL-12760 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12010 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1829 | 3 | 0000 | SH-12010 | SHA-12010B |  | SHOWER/EYEWASH ACTIVATION ALARM 12010 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1830 | 1 | 0003 | SH-12010 | SHA-12010C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12010 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1831 | 4 | 1200 | SH-12011 | FSH-12761 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12011 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1832 | 4 | 1200 | SH-12011 | FAH-12761 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1833 | 4 | 1200 | SH-12011 | FO-12761 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1834 | 4 | 1200 | SH-12011 | UK-12761 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12011 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1835 | 4 | 1200 | SH-12011 | UL12761 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12011 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1836 | 3 | 0000 | SH-12011 | SHA-12011B |  | SHOWER/EYEWASH ACTIVATION ALARM 12011 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1837 | 1 | 0003 | SH-12011 | SHA-12011C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12011 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1838 | 4 | 1200 | SH-12012 | FSH-12762 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12012 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1839 | 4 | 1200 | SH-12012 | FAH-12762 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1840 | 4 | 1200 | SH-12012 | FO-12762 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1841 | 4 | 1200 | SH-12012 | UK-12762 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12012 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1842 | 4 | 1200 | SH-12012 | UL-12762 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12012 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1843 | 3 | 0000 | SH-12012 | SHA-12012B |  | SHOWER/EYEWASH ACTIVATION ALARM 12012 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1844 | 1 | 0003 | SH-12012 | SHA-12012C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12012 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1845 | 4 | 1200 | SH-12013 | FSH-12763 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-12013 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 |  |  |  | Replaced with 1200JND77
1846 | 4 | 1200 | SH-12013 | FAH-12763 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1847 | 4 | 1200 | SH-12013 | FO-12763 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1848 | 4 | 1200 | SH-12013 | UK-12763 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12013 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1849 | 4 | 1200 | SH-12013 | UL-12763 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-12013 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1850 | 3 | 0000 | SH-12013 | SHA-12013B |  | SHOWER/EYEWASH ACTIVATION ALARM 12013 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND12 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1851 | 1 | 0003 | SH-12013 | SHA-12013C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 12013 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1852 | 4 | 1300 | SH-13001 | FSH-13751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-13001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced with 2300JND84
1853 | 4 | 1300 | SH-13001 | FAH-13751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1854 | 4 | 1300 | SH-13001 | FO-13751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1855 | 4 | 1300 | SH-13001 | UK-13751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1856 | 4 | 1300 | SH-13001 | UL-13751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1857 | 3 | 0000 | SH-13001 | SHA-13001B |  | SHOWER/EYEWASH ACTIVATION ALARM 13001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1858 | 1 | 0003 | SH-13001 | SHA-13001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 13001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1859 | 4 | 1300 | SH-13002 | FSH-13752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-13002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced with 2300JND84
1860 | 4 | 1300 | SH-13002 | FAH-13752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1861 | 4 | 1300 | SH-13002 | FO-13752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1862 | 4 | 1300 | SH-13002 | UK-13752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1863 | 4 | 1300 | SH-13002 | UL-13752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1864 | 3 | 0000 | SH-13002 | SHA-13002B |  | SHOWER/EYEWASH ACTIVATION ALARM 13002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1865 | 1 | 0003 | SH-13002 | SHA-13002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 13002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1866 | 4 | 1300 | SH-13003 | FSH-13753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-13003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced with 2300JND84
1867 | 4 | 1300 | SH-13003 | FAH-13753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1868 | 4 | 1300 | SH-13003 | FO-13753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1869 | 4 | 1300 | SH-13003 | UK-13753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1870 | 4 | 1300 | SH-13003 | UL-13753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1871 | 3 | 0000 | SH-13003 | SHA-13003B |  | SHOWER/EYEWASH ACTIVATION ALARM 13003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1872 | 1 | 0003 | SH-13003 | SHA-13003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 13003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1873 | 4 | 1300 | SH-13004 | FSH-13754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | 2300JND84 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced with 2300JND84
1874 | 4 | 1300 | SH-13004 | FAH-13754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1875 | 4 | 1300 | SH-13004 | FO-13754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1876 | 4 | 1300 | SH-13004 | UK-13754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1877 | 4 | 1300 | SH-13004 | UL-13754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1878 | 3 | 0000 | SH-13004 | SHA-13004B |  | SHOWER/EYEWASH ACTIVATION ALARM 13004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1879 | 1 | 0003 | SH-13004 | SHA-13004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 13004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1880 | 4 | 1300 | SH-13005 | FSH-13755 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-13005 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced with 2300JND84
1881 | 4 | 1300 | SH-13005 | FAH-13755 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1882 | 4 | 1300 | SH-13005 | FO-13755 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1883 | 4 | 1300 | SH-13005 | UK-13755 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13005 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1884 | 4 | 1300 | SH-13005 | UL-13755 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-13005 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1885 | 3 | 0000 | SH-13005 | SHA-13005B |  | SHOWER/EYEWASH ACTIVATION ALARM 13005 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1886 | 1 | 0003 | SH-13005 | SHA-13005C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 13005 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1887 | 4 | 2300 | SH-23001 | FSH-23751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-23001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced with 2300JND84
1888 | 4 | 2300 | SH-23001 | FAH-23751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1889 | 4 | 2300 | SH-23001 | FO-23751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1890 | 4 | 2300 | SH-23001 | UK-23751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1891 | 4 | 2300 | SH-23001 | UL-23751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1892 | 3 | 0000 | SH-23001 | SHA-23001B |  | SHOWER/EYEWASH ACTIVATION ALARM 23001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND13 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1893 | 1 | 0003 | SH-23001 | SHA-23001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 23001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1894 | 4 | 2300 | SH-23002 | FSH-23752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-23002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced with 2300JND84
1895 | 4 | 2300 | SH-23002 | FAH-23752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1896 | 4 | 2300 | SH-23002 | FO-23752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1897 | 4 | 2300 | SH-23002 | UK-23752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1898 | 4 | 2300 | SH-23002 | UL-23752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1899 | 3 | 0000 | SH-23002 | SHA-23002B |  | SHOWER/EYEWASH ACTIVATION ALARM 23002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1900 | 1 | 0003 | SH-23002 | SHA-23002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 23002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1901 | 4 | 2300 | SH-23003 | FSH-23753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-23003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced with 2300JND84
1902 | 4 | 2300 | SH-23003 | FAH-23753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1903 | 4 | 2300 | SH-23003 | FO-23753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1904 | 4 | 2300 | SH-23003 | UK-23753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1905 | 4 | 2300 | SH-23003 | UL-23753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1906 | 3 | 0000 | SH-23003 | SHA-23003B |  | SHOWER/EYEWASH ACTIVATION ALARM 23003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1907 | 1 | 0003 | SH-23003 | SHA-23003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 23003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1908 | 4 | 2300 | SH-23004 | FSH-23754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-23004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced with 2300JND84
1909 | 4 | 2300 | SH-23004 | FAH-23754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1910 | 4 | 2300 | SH-23004 | FO-23754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1911 | 4 | 2300 | SH-23004 | UK-23754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1912 | 4 | 2300 | SH-23004 | UL-23754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1913 | 3 | 0000 | SH-23004 | SHA-23004B |  | SHOWER/EYEWASH ACTIVATION ALARM 23004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1914 | 1 | 0003 | SH-23004 | SHA-23004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 23004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1915 | 4 | 2300 | SH-23005 | FSH-23755 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-23005 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced with 2300JND84
1916 | 4 | 2300 | SH-23005 | FAH-23755 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1917 | 4 | 2300 | SH-23005 | FO-23755 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1918 | 4 | 2300 | SH-23005 | UK-23755 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23005 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1919 | 4 | 2300 | SH-23005 | UL-23755 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-23005 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1920 | 3 | 0000 | SH-23005 | SHA-23005B |  | SHOWER/EYEWASH ACTIVATION ALARM 23005 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND29 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1921 | 1 | 0003 | SH-23005 | SHA-23005C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 23005 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1922 | 4 | 1400 | SH-14001 | FSH-14751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-14001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced with 1400JND93
1923 | 4 | 1400 | SH-14001 | FAH-14751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1924 | 4 | 1400 | SH-14001 | FO-14751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1925 | 4 | 1400 | SH-14001 | UK-14751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1926 | 4 | 1400 | SH-14001 | UL-14751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2758 | 0 | 0000 | SH-14001 | SHA-14001B |  | SHOWER/EYEWASH ACTIVATION ALARM 14001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1927 | 1 | 0003 | SH-14001 | SHA-14001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 14001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1928 | 4 | 1400 | SH-14002 | FSH-14752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-14002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced with 1400JND93
1929 | 4 | 1400 | SH-14002 | FAH-14752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1930 | 4 | 1400 | SH-14002 | FO-14752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1931 | 4 | 1400 | SH-14002 | UK-14752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1932 | 4 | 1400 | SH-14002 | UL-14752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2763 | 0 | 0000 | SH-14002 | SHA-14002B |  | SHOWER/EYEWASH ACTIVATION ALARM 14002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1933 | 1 | 0003 | SH-14002 | SHA-14002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 14002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1934 | 4 | 1400 | SH-14003 | FSH-14753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-14003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced with 1400JND93
1935 | 4 | 1400 | SH-14003 | FAH-14753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1936 | 4 | 1400 | SH-14003 | FO-14753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1937 | 4 | 1400 | SH-14003 | UK-14753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1938 | 4 | 1400 | SH-14003 | UL-14753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2768 | 0 | 0000 | SH-14003 | SHA-14003B |  | SHOWER/EYEWASH ACTIVATION ALARM 14003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1939 | 1 | 0003 | SH-14003 | SHA-14003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 14003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1940 | 4 | 1400 | SH-14004 | FSH-14754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-14004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced with 1400JND93
1941 | 4 | 1400 | SH-14004 | FAH-14754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1942 | 4 | 1400 | SH-14004 | FO-14754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1943 | 4 | 1400 | SH-14004 | UK-14754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1944 | 4 | 1400 | SH-14004 | UL-14754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2773 | 0 | 0000 | SH-14004 | SHA-14004B |  | SHOWER/EYEWASH ACTIVATION ALARM 14004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1945 | 1 | 0003 | SH-14004 | SHA-14004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 14004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1946 | 4 | 1400 | SH-14005 | FSH-14755 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-14005 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced with 1400JND93
1947 | 4 | 1400 | SH-14005 | FAH-14755 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1948 | 4 | 1400 | SH-14005 | FO-14755 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1949 | 4 | 1400 | SH-14005 | UK-14755 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14005 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1950 | 4 | 1400 | SH-14005 | UL-14755 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-14005 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2778 | 0 | 0000 | SH-14005 | SHA-14005B |  | SHOWER/EYEWASH ACTIVATION ALARM 14005 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND14 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1951 | 1 | 0003 | SH-14005 | SHA-14005C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 14005 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1952 | 4 | 1500 | SH-15001 | FSH-15751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-15001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1501
1953 | 4 | 1500 | SH-15001 | FAH-15751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1954 | 4 | 1500 | SH-15001 | FO-15751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1955 | 4 | 1500 | SH-15001 | UK-15751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-15001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1956 | 4 | 1500 | SH-15001 | UL-15751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-15001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1957 | 1 | 0000 | SH-15001 | SHA-15001B |  | SHOWER/EYEWASH ACTIVATION ALARM 15001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1958 | 1 | 0003 | SH-15001 | SHA-15001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 15001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1959 | 4 | 1600 | SH-16001 | FSH-16751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1960 | 4 | 1600 | SH-16001 | FAH-16751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1961 | 4 | 1600 | SH-16001 | FO-16751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1962 | 4 | 1600 | SH-16001 | UK-16751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1963 | 4 | 1600 | SH-16001 | UL-16751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1964 | 3 | 0000 | SH-16001 | SHA-16001B |  | SHOWER/EYEWASH ACTIVATION ALARM 16001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1965 | 1 | 0003 | SH-16001 | SHA-16001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1966 | 4 | 1600 | SH-16002 | FSH-16752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1967 | 4 | 1600 | SH-16002 | FAH-16752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1968 | 4 | 1600 | SH-16002 | FO-16752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1969 | 4 | 1600 | SH-16002 | UK-16752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1970 | 4 | 1600 | SH-16002 | UL-16752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1971 | 3 | 0000 | SH-16002 | SHA-16002B |  | SHOWER/EYEWASH ACTIVATION ALARM 16002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1972 | 1 | 0003 | SH-16002 | SHA-16002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1973 | 4 | 1600 | SH-16003 | FSH-16753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1974 | 4 | 1600 | SH-16003 | FAH-16753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1975 | 4 | 1600 | SH-16003 | FO-16753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1976 | 4 | 1600 | SH-16003 | UK-16753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1977 | 4 | 1600 | SH-16003 | UL-16753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1978 | 3 | 0000 | SH-16003 | SHA-16003B |  | SHOWER/EYEWASH ACTIVATION ALARM 16003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1979 | 1 | 0003 | SH-16003 | SHA-16003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1980 | 4 | 1600 | SH-16004 | FSH-16754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1981 | 4 | 1600 | SH-16004 | FAH-16754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1982 | 4 | 1600 | SH-16004 | FO-16754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1983 | 4 | 1600 | SH-16004 | UK-16754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1984 | 4 | 1600 | SH-16004 | UL-16754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1985 | 3 | 0000 | SH-16004 | SHA-16004B |  | SHOWER/EYEWASH ACTIVATION ALARM 16004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1986 | 1 | 0003 | SH-16004 | SHA-16004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1987 | 4 | 1600 | SH-16005 | FSH-16755 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16005 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1988 | 4 | 1600 | SH-16005 | FAH-16755 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1989 | 4 | 1600 | SH-16005 | FO-16755 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1990 | 4 | 1600 | SH-16005 | UK-16755 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16005 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1991 | 4 | 1600 | SH-16005 | UL-16755 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16005 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1992 | 3 | 0000 | SH-16005 | SHA-16005B |  | SHOWER/EYEWASH ACTIVATION ALARM 16005 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
1993 | 1 | 0003 | SH-16005 | SHA-16005C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16005 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
1994 | 4 | 1600 | SH-16006 | FSH-16756 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-16006 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1601 |  |  |  | Replaced with 1600JND80
1995 | 4 | 1600 | SH-16006 | FAH-16756 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
1996 | 4 | 1600 | SH-16006 | FO-16756 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
1997 | 4 | 1600 | SH-16006 | UK-16756 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16006 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1998 | 4 | 1600 | SH-16006 | UL-16756 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-16006 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
1999 | 3 | 0000 | SH-16006 | SHA-16006B |  | SHOWER/EYEWASH ACTIVATION ALARM 16006 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2000 | 1 | 0003 | SH-16006 | SHA-16006C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 16006 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2001 | 4 | 2600 | SH-26001 | FSH-26751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-26001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2002 | 4 | 2600 | SH-26001 | FAH-26751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2003 | 4 | 2600 | SH-26001 | FO-26751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2004 | 4 | 2600 | SH-26001 | UK-26751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2005 | 4 | 2600 | SH-26001 | UL-26751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2006 | 3 | 0000 | SH-26001 | SHA-26001B |  | SHOWER/EYEWASH ACTIVATION ALARM 26001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2007 | 1 | 0003 | SH-26001 | SHA-26001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 26001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2008 | 4 | 2600 | SH-26002 | FSH-26752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-26002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2009 | 4 | 2600 | SH-26002 | FAH-26752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2010 | 4 | 2600 | SH-26002 | FO-26752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2011 | 4 | 2600 | SH-26002 | UK-26752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2012 | 4 | 2600 | SH-26002 | UL-26752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2013 | 3 | 0000 | SH-26002 | SHA-26002B |  | SHOWER/EYEWASH ACTIVATION ALARM 26002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2014 | 1 | 0003 | SH-26002 | SHA-26002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 26002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2015 | 4 | 2600 | SH-26003 | FSH-26753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-26003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2016 | 4 | 2600 | SH-26003 | FAH-26753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2017 | 4 | 2600 | SH-26003 | FO-26753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2018 | 4 | 2600 | SH-26003 | UK-26753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2019 | 4 | 2600 | SH-26003 | UL-26753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-26003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2020 | 3 | 0000 | SH-26003 | SHA-26003B |  | SHOWER/EYEWASH ACTIVATION ALARM 26003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2021 | 1 | 0003 | SH-26003 | SHA-26003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 26003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2022 | 4 | 3600 | SH-36001 | FSH-36751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-36001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2023 | 4 | 3600 | SH-36001 | FAH-36751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2024 | 4 | 3600 | SH-36001 | FO-36751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2025 | 4 | 3600 | SH-36001 | UK-36751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2026 | 4 | 3600 | SH-36001 | UL-36751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2027 | 3 | 0000 | SH-36001 | SHA-36001B |  | SHOWER/EYEWASH ACTIVATION ALARM 36001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2028 | 3 | 0003 | SH-36001 | SHA-36001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 36001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2029 | 4 | 3600 | SH-36002 | FSH-36752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-36002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2030 | 4 | 3600 | SH-36002 | FAH-36752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2031 | 4 | 3600 | SH-36002 | FO-36752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2032 | 4 | 3600 | SH-36002 | UK-36752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2033 | 4 | 3600 | SH-36002 | UL-36752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2034 | 3 | 0000 | SH-36002 | SHA-36002B |  | SHOWER/EYEWASH ACTIVATION ALARM 36002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2035 | 3 | 0003 | SH-36002 | SHA-36002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 36002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2036 | 4 | 3600 | SH-36003 | FSH-36753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-36003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2037 | 4 | 3600 | SH-36003 | FAH-36753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2038 | 4 | 3600 | SH-36003 | FO-36753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2039 | 4 | 3600 | SH-36003 | UK-36753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2040 | 4 | 3600 | SH-36003 | UL-36753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2041 | 3 | 0000 | SH-36003 | SHA-36003B |  | SHOWER/EYEWASH ACTIVATION ALARM 36003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2042 | 3 | 0003 | SH-36003 | SHA-36003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 36003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2043 | 4 | 3600 | SH-36004 | FSH-36754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-36004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2601 |  |  |  | Replaced with 1600JND80
2044 | 4 | 3600 | SH-36004 | FAH-36754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2045 | 4 | 3600 | SH-36004 | FO-36754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2046 | 4 | 3600 | SH-36004 | UK-36754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2047 | 4 | 3600 | SH-36004 | UL-36754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-36004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2048 | 4 | 0000 | SH-36004 | SHA-36004B |  | SHOWER/EYEWASH ACTIVATION ALARM 36004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 15 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2049 | 4 | 0003 | SH-36004 | SHA-36004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 36004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2050 | 4 | 4600 | SH-46001 | FSH-46751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-46001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 |  |  |  | Replaced with 1600JND80
2051 | 4 | 4600 | SH-46001 | FAH-46751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2052 | 4 | 4600 | SH-46001 | FO-46751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2053 | 4 | 4600 | SH-46001 | UK-46751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2054 | 4 | 4600 | SH-46001 | UL-46751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2055 | 3 | 0000 | SH-46001 | SHA-46001B |  | SHOWER/EYEWASH ACTIVATION ALARM 46001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2056 | 1 | 0003 | SH-46001 | SHA-46001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 46001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2057 | 4 | 4600 | SH-46002 | FSH-46752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-46002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 |  |  |  | Replaced with 1600JND80
2058 | 4 | 4600 | SH-46002 | FAH-46752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2059 | 4 | 4600 | SH-46002 | FO-46752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2060 | 4 | 4600 | SH-46002 | UK-46752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2061 | 4 | 4600 | SH-46002 | UL-46752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2062 | 3 | 0000 | SH-46002 | SHA-46002B |  | SHOWER/EYEWASH ACTIVATION ALARM 46002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND16 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2063 | 1 | 0003 | SH-46002 | SHA-46002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 46002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2064 | 4 | 4600 | SH-46003 | FSH-46753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-46003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 |  |  |  | Replaced with 1600JND80
2065 | 4 | 4600 | SH-46003 | FAH-46753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2066 | 4 | 4600 | SH-46003 | FO-46753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2067 | 4 | 4600 | SH-46003 | UK-46753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2068 | 4 | 4600 | SH-46003 | UL-46753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2069 | 3 | 0000 | SH-46003 | SHA-46003B |  | SHOWER/EYEWASH ACTIVATION ALARM 46003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2070 | 3 | 0003 | SH-46003 | SHA-46003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 46003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2071 | 4 | 4600 | SH-46004 | FSH-46754 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | FRR | d | F | SH-46004 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-4601 |  |  |  | Replaced with 1600JND80
2072 | 4 | 4600 | SH-46004 | FAH-46754 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2073 | 4 | 4600 | SH-46004 | FO-46754 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2074 | 4 | 4600 | SH-46004 | UK-46754 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46004 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2075 | 4 | 4600 | SH-46004 | UL-46754 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-46004 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2076 | 3 | 0000 | SH-46004 | SHA-46004B |  | SHOWER/EYEWASH ACTIVATION ALARM 46004 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2077 | 3 | 0003 | SH-46004 | SHA-46004C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 46004 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2078 | 4 | 1700 | SH-17001 | FSH-17751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-17001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1701
2079 | 4 | 1700 | SH-17001 | FAH-17751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2080 | 4 | 1700 | SH-17001 | FO-17751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2081 | 4 | 1700 | SH-17001 | UK-17751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-17001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2082 | 4 | 1700 | SH-17001 | UL-17751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-17001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2868 | 0 | 0000 | SH-17001 | SHA-17001B |  | SHOWER/EYEWASH ACTIVATION ALARM 17001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND17 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2083 | 1 | 0003 | SH-17001 | SHA-17001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 17001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2084 | 4 | 1900 | SH-19001 | FSH-19751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-19001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1901
2085 | 4 | 1900 | SH-19001 | FAH-19751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2086 | 4 | 1900 | SH-19001 | FO-19751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2087 | 4 | 1900 | SH-19001 | UK-19751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-19001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2088 | 4 | 1900 | SH-19001 | UL-19751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-19001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2873 | 0 | 0000 | SH-19001 | SHA-19001B |  | SHOWER/EYEWASH ACTIVATION ALARM 19001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND18 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2089 | 1 | 0003 | SH-19001 | SHA-19001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 19001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2090 | 4 | 2100 | SH-21001 | FSH-21751 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-21001 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2101 |  |  |  | Replaced with2100JND70
2091 | 4 | 2100 | SH-21001 | FAH-21751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2092 | 4 | 2100 | SH-21001 | FO-21751 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2093 | 4 | 2100 | SH-21001 | UK-21751 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21001 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2094 | 4 | 2100 | SH-21001 | UL-21751 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21001 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2878 | 0 | 0000 | SH-21001 | SHA-21001B |  | SHOWER/EYEWASH ACTIVATION ALARM 21001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND19 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2095 | 1 | 0003 | SH-21001 | SHA-21001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 21001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2096 | 4 | 2100 | SH-21002 | FSH-21752 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-21002 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2101 |  |  |  | Replaced with2100JND70
2097 | 4 | 2100 | SH-21002 | FAH-21752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2098 | 4 | 2100 | SH-21002 | FO-21752 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2099 | 4 | 2100 | SH-21002 | UK-21752 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21002 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2100 | 4 | 2100 | SH-21002 | UL-21752 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21002 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2883 | 0 | 0000 | SH-21002 | SHA-21002B |  | SHOWER/EYEWASH ACTIVATION ALARM 21002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND19 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2101 | 1 | 0003 | SH-21002 | SHA-21002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 21002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2102 | 4 | 2100 | SH-21003 | FSH-21753 | Safety Shower and Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | FGDS | CRR | d | F | SH-21003 | 1 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2101 |  |  |  | Replaced with2100JND70
2103 | 4 | 2100 | SH-21003 | FAH-21753 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2104 | 4 | 2100 | SH-21003 | FO-21753 | Safety Shower and Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2105 | 4 | 2100 | SH-21003 | UK-21753 |  |  | Becaon located on Safety Shower | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21003 | 2 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2106 | 4 | 2100 | SH-21003 | UL-21753 |  |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-UDD-0005 | DO | NIS | FGDS | CRR | d | F | SH-21003 | 3 | 04-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2888 | 0 | 0000 | SH-21003 | SHA-21003B |  | SHOWER/EYEWASH ACTIVATION ALARM 21003 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND19 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2107 | 1 | 0003 | SH-21003 | SHA-21003C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 21003 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2108 | 3 | 1000 | EW-1001 | FSH-10751A | Status signal Flow switch for Safety Eye wash | Signal from LFAP to FGS | Flow switch High | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2109 | 1 | 1000 | EW-1001 | FAH-10751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2110 | 1 | 1000 | EW-1001 | FO-10751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2111 | 3 | 0000 | EW-1001 | EWA-1001B |  | SHOWER/EYEWASH ACTIVATION ALARM 1001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2112 | 1 | 0003 | EW-1001 | EWA-1001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 1001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2113 | 3 | 1000 | EW-1002 | FSH-10752A | Status signal Flow switch for Safety Eye wash | Signal from LFAP to FGS | Flow switch High | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2114 | 2 | 1000 | EW-1002 | FAH-10752 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2115 | 2 | 1000 | EW-1002 | FO-10752 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2116 | 3 | 0000 | EW-1002 | EWA-1002B |  | SHOWER/EYEWASH ACTIVATION ALARM 1002 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2117 | 2 | 0003 | EW-1002 | EWA-1002C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM 1002 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2118 | 3 | 2000 | EW-2001 | FSH-20751 | Status signal Flow switch for Safety Eye wash | Signal from LFAP to FGS | Flow switch High | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2
2119 | 1 | 2000 | EW-2001 | FAH-20751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2120 | 1 | 2000 | EW-2001 | FO-20751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2121 | 3 | 0000 | EW-2001 | EWA-2001B |  | SHOWER/EYEWASH ACTIVATION ALARM MCC 2001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2122 | 1 | 0003 | EW-2001 | EWA-2001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM MCC 2001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2123 | 3 | 4000 | EW-3001 | FSH-30751A | Status signal Flow switch for Safety Eye wash | Signal from LFAP to FGS | Flow switch High | ESBR-HS-CAF-0007 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2124 | 1 | 4000 | EW-3001 | FAH-30751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2125 | 1 | 4000 | EW-3001 | FO-30751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2126 | 3 | 0000 | EW-3001 | EWA-3001B |  | SHOWER/EYEWASH ACTIVATION ALARM FINISHING AREA 3001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2127 | 1 | 0003 | EW-3001 | EWA-3001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM FINISHING AREA 3001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2128 | 3 | 5000 | EW-4001 | FSH-40751A | Status signal Flow switch for Safety Eye wash | Signal from LFAP to FGS | Flow switch High | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 15 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203
2129 | 1 | 5000 | EW-4001 | FAH-40751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
2130 | 1 | 5000 | EW-4001 | FO-40751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
2131 | 3 | 0000 | EW-4001 | EWA-4001B |  | SHOWER/EYEWASH ACTIVATION ALARM MAIN WORKSHOP 4001 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2132 | 1 | 0003 | EW-4001 | EWA-4001C | Signal connection through remote I/O | SHOWER/EYEWASH ACTIVATION ALARM MAIN WORKSHOP 4001 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2133 | 2 | 6000 | IRGD-6001 | IRGD/P-6001 | Control Room Air Lock | Point Type Gas Detector | Flammable. Gas (HVAC Room) Prepration | ESBR-HS-LYT-0019 | AIR | NIS | FGDS | CRR | d | F | IRGD-6001 |  | 01-T-1.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2134 | 2 | 6000 | IRGD-6001 | IRGAH-6001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-LYT-0019 | [5 empty] | MW | [10 empty] | %LFL |  | 10
2135 | 2 | 6000 | IRGD-6001 | IRGAHHP6001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-LYT-0019 | [5 empty] | MW | [10 empty] | %LFL | 25
2136 | 2 | 6000 | IRGD-6001 | XA-6001 | Status signal to FGS |  | Fault | ESBR-HS-CAF-0006 | DI | NIS | FGDS | CRR | d | F | 6000JND75 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2137 | 3 | 0000 | IRGD-6000 | IRGA-6000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 6000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2138 | 2 | 0003 | IRGD-6000 | IRGA-6000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 6000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2139 | 2 | 6000 | IRGD-6002 | IRGD/P-6002 | Control Room Air Lock | Point Type Gas Detector | Flammable. Gas (HVAC Room) Prepration | ESBR-HS-LYT-0019 | AIR | NIS | FGDS | CRR | d | F | IRGD-6002 |  | 01-T-1.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39/40 | EXT/24Vdc |  |  | 0 | 100 | %LFL |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2140 | 2 | 6000 | IRGD-6002 | IRGAH-6002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-LYT-0019 | [5 empty] | MW | [10 empty] | %LFL |  | 10
2141 | 2 | 6000 | IRGD-6002 | IRGAHHP6002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-LYT-0019 | [5 empty] | MW | [10 empty] | %LFL | 25
2142 | 2 | 6000 | IRGD-6002 | XA-6002 | Status signal to FGS |  | Fault | ESBR-HS-CAF-0006 | DI | NIS | FGDS | CRR | d | F | 6000JND75 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2143 | 2 | 6000 | TGD-6001 | TGD-6001 | AIR LOCK |  | Toxic Gas (HVAC Room) Prepration | ESBR-HS-LYT-0019 | AIR | NIS | LFAP | CRR | d | F | TGD-6001 |  | 01-T-1.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | (TLV-TWA) |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2144 | 2 | 6000 | TGD-6001 | TGAH-6001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-LYT-0019 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
2145 | 2 | 6000 | TGD-6001 | TGAHH-6001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-LYT-0019 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
2146 | 2 | 6000 | TGD-6001 | XA-6003 |  |  | Fault Signal, Toxic, Prepration area | ESBR-HS-CAF-0006 | DI | NIS | FGDS | CRR | d | F | 6000JND75 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2147 | 3 | 0000 | TGD-6000 | TGA-6000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 6000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2148 | 3 | 0003 | TGD-6000 | TGA-6000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 6000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2149 | 2 | 6000 | TGD-6002 | TGD-6002 | AIR LOCK |  | Toxic Gas (HVAC Room) Prepration | ESBR-HS-LYT-0019 | AIR | NIS | LFAP | CRR | d | F | TGD-6002 |  | 01-T-1.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /39/40 | EXT/24Vdc |  |  | 0 | 100 | (TLV-TWA) |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2150 | 2 | 6000 | TGD-6002 | TGAH-6002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-LYT-0019 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
2151 | 2 | 6000 | TGD-6002 | TGAHH-6002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-LYT-0019 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
2152 | 2 | 6000 | TGD-6002 | XA-6004 |  |  | Fault Signal, Toxic, Prepration area | ESBR-HS-CAF-0006 | DI | NIS | FGDS | CRR | d | F | 6000JND75 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2153 | 2 | 6000 | UK-6001 | UK-6001A | AUDIBLE ALARM (CONTINUOUS ) | Deluge Valve System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2154 | 2 | 6000 | UK-6001 | UK-6001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2155 | 2 | 6000 | UK-6001 | UK-6001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/41 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2156 | 2 | 6000 | UL-6001 | UL-6001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 5,7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2157 | 2 | 6000 | UL-6001 | UL-6001B | (RED FLASHING LIGHT) | Deluge Valve System,MCP | FLASHING LIGHT | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 6,7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2158 | 2 | 6000 | UL-6001 | UL-6001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0019 | DO | NIS | FGDS | CRR | d | F | 6000JND70 | 7,7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010 /45 | EXT/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2159 | 3 | 6000 | MCP-6001 | MCP-6001 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND70 | 4 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2160 | 3 | 6000 | MCP-6002 | MCP-6002 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2161 | 3 | 6000 | MCP-6003 | MCP-6003 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT(VFD ROOM) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2162 | 3 | 6000 | MCP-6004 | MCP-6004 | Activation of Continues audible alarm | Activation of Red Falshing Light | MANUAL CALL POINT(VFD ROOM) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 12 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/47 | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2163 | 3 | 0000 | MCP-6000 | MCP-6000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 6000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2164 | 3 | 0003 | MCP-6000 | MCP-6000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 6000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2165 | 3 | 6000 | SD-6006 | SD-6001 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (Control Room) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2166 | 3 | 6000 | SD-6006 | SD-6003 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (Control Room) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2167 | 3 | 6000 | SD-6006 | SD-6004 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (Control Room) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2168 | 3 | 6000 | SD-6006 | SD-6002 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (Control Room) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2169 | 3 | 6000 | SD-6006 | SD-6005 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (VFD ROOM) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2170 | 3 | 6000 | SD-6006 | SD-6006 | Activation of Continues audible alarm | Activation of Red Falshing Light | Smoke detector (VFD ROOM) | ESBR-HS-LYT-0019 | DIR | NIS | FGDS | CRR | d | F | 6000JND75 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN |  | 0 | 100 | % |  |  |  |  | ESBR-CI-DWG-1203 | ESBR-CI-DAS-0030
2171 | 3 | 0000 | HS-1070 | HS-1070B | General Alarm sounder Matrix Panel CCR | Hand Switch | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND15 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN
2172 | 3 | 0001 | HS-3070 | HS-3070F | General Alarm sounder Matrix Panel Finishing | Buzzer | Hand Switch (FRR) | ESBR-HS-CAF-0005 | DIR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [12 empty] | Changed from 73
2173 | 4 | 0002 | MCP-6000 | MCP-6000P |  | MANUAL CALL POINT STATUS LAMP OF AREA 6000 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2174 | 3 | 0000 | UK-1070 | UK-1070B | Buzare Matrix Panel CCR | Buzzer | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE
2175 | 3 | 0000 | UK-1070 | HS-1071B | Acknowlege | Hand switch | Matrix Panel Hand switch(CRR) | ESBR-HS-CAF-0002 | DI | NIS | FGDS | CRR |  | MP | 1000CND15 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN
2176 | 3 | 0001 | UK-1070 | UK-3070F | Buzare Matrix Panel Finishing | Hand switch | Buzare(FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE | [12 empty] | Changed from 73
2177 | 3 | 0001 | UK-3070 | HS-3071F | Acknowlege | Hand switch | Matrix Panel Hand switch(FRR) | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FCR |  | MPF | 3000CND77 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [12 empty] | Changed from 73
2178 | 3 | 0002 | DV-12001 | HS-12701P |  | HAND SWITCH(PREPARATION CONTROL ROOM) 12001 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 1 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
2179 | 4 | 0002 | SD-6000 | SA-6000P | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 6000 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2180 | 3 | 0000 | UL-1070 | UL-1070AB | General Falshing light on Matrix Panel | (YELLOW FLASHING LIGHT) Matrix Panel | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE
2181 | 3 | 0000 | UL-1070 | UL-1070BB | General Falshing light on Matrix Panel | (RED FLASHING LIGHT) Matrix Panel | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE
2182 | 3 | 0000 | UL-1070 | UL-1070CB | General Falshing light on Matrix Panel | (GREEN FLASHING LIGHT) Matrix Panel | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND15 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE
2183 | 3 | 0001 | UL-3070 | UL-3070AF | Finishing Room | General Falshing light on Matrix Panel | (YELLOW FLASHING LIGHT) Matrix Panel (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE | [12 empty] | Changed from 73
2184 | 3 | 0001 | UL-3070 | UL-3070BF | Finishing Room | General Falshing light on Matrix Panel | (RED FLASHING LIGHT) Matrix Panel (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE | [12 empty] | Changed from 73
2185 | 3 | 0001 | UL-3070 | UL-3070CF | Finishing Room | General Falshing light on Matrix Panel | (GREEN FLASHING LIGHT) Matrix Panel (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | CLOSE | [12 empty] | Changed from 73
2186 | 3 | 0002 | DV-12001 | PAL-12701P |  | HAND SWITCH(CONTROL ROOM) 12002 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2187 | 4 | 0002 | IRGD-6000 | IRGA-6000P | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 6000 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2188 | 3 | 0002 | DV-12001 | PAH-12701P |  | DELUGE VALVE RELEASE STATUS LAMP 12001 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2189 | 3 | 0001 | MCP-15000 | MCP-15000F |  | MANUAL CALL POINT STATUS LAMP OF AREA 1500 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2190 | 3 | 0001 | MCP-16000 | MCP-16000F |  | MANUAL CALL POINT STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2191 | 3 | 0001 | HD-26000 | HA-26000F | Smoke and fir, Signal to FCR | HEAT DETECTOR STATUS LAMP OF FIRE ZONE 1600,2600,3600,4600 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2192 | 2 | 0001 | FD-16000 | FAH-16000F | Fire and Gas, Signal to FCR | FIRE DETECTOR STATUS LAMP OF AREA 1600,2600,3600,4600 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2193 | 3 | 0001 | HVAC-3000 | MKHL-Y3000F |  | HVAC SHUTDOWN STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND74 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from JND70
2194 | 4 | 0001 | DV-16030 | HS-16730F |  | HAND SWITCH(FINISHING CONTROL ROOM) 16001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 5 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Changed from 71
2195 | 2 | 0001 | DV-16001 | PAL-16701F |  | FUSIBLE LINK MELTED STATUS LAMP 16001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2196 | 2 | 0001 | DV-16001 | PAH-16701F |  | DELUGE VALVE RELEASE STATUS LAMP 16001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2197 | 2 | 0001 | DV-26030 | HS-26730F |  | HAND SWITCH(FINISHING CONTROL ROOM) 16002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 8 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Changed from 71
2198 | 2 | 0001 | DV-16002 | PAL-16702F |  | HAND SWITCH(CONTROL ROOM) 16002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2199 | 2 | 0001 | DV-16002 | PAH-16702F |  | FUSIBLE LINK MELTED STATUS LAMP 16002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2200 | 4 | 0001 | DV-36030 | HS-36730F |  | HAND SWITCH(FINISHING CONTROL ROOM) 36001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 11 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Changed from 71
2201 | 2 | 0001 | DV-36001 | PAL-36701F |  | FUSIBLE LINK MELTED STATUS LAMP 36001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2202 | 2 | 0001 | DV-36001 | PAH-36701F |  | DELUGE VALVE RELEASE STATUS LAMP 36001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 71
2203 | 4 | 0001 | DV-46030 | HS-46730F |  | HAND SWITCH(FINISHING CONTROL ROOM) 36002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | FCR |  | MPF | 3000CND75 | 14 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Changed from 71
2204 | 2 | 0001 | DV-36002 | PAL-36702F |  | FUSIBLE LINK MELTED STATUS LAMP 36002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2205 | 2 | 0001 | DV-36002 | PAH-36702F |  | DELUGE VALVE RELEASE STATUS LAMP 36002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2206 | 2 | 0001 | SH-15001 | SHA-15001F |  | SHOWER/EYEWASH ACTIVATION ALARM 15001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2207 | 2 | 0001 | SH-16001 | SHA-16001F |  | SHOWER/EYEWASH ACTIVATION ALARM 16001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2208 | 2 | 0001 | SH-16002 | SHA-16002F |  | SHOWER/EYEWASH ACTIVATION ALARM 16002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2209 | 2 | 0001 | SH-16003 | SHA-16003F |  | SHOWER/EYEWASH ACTIVATION ALARM 16003 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2210 | 2 | 0001 | SH-16004 | SHA-16004F |  | SHOWER/EYEWASH ACTIVATION ALARM 16004 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2211 | 2 | 0001 | SH-16005 | SHA-16005F |  | SHOWER/EYEWASH ACTIVATION ALARM 16005 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2212 | 2 | 0001 | SH-16006 | SHA-16006F |  | SHOWER/EYEWASH ACTIVATION ALARM 16006 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2213 | 2 | 0001 | SH-26001 | SHA-26001F |  | SHOWER/EYEWASH ACTIVATION ALARM 26001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2214 | 2 | 0001 | SH-26002 | SHA-26002F |  | SHOWER/EYEWASH ACTIVATION ALARM 26002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2215 | 2 | 0001 | SH-26003 | SHA-26003F |  | SHOWER/EYEWASH ACTIVATION ALARM 26003 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2216 | 4 | 0001 | SH-36001 | SHA-36001F |  | SHOWER/EYEWASH ACTIVATION ALARM 36001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2217 | 4 | 0001 | SH-36002 | SHA-36002F |  | SHOWER/EYEWASH ACTIVATION ALARM 36002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2218 | 4 | 0001 | SH-36003 | SHA-36003F |  | SHOWER/EYEWASH ACTIVATION ALARM 36003 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2219 | 4 | 0001 | SH-36004 | SHA-36004F |  | SHOWER/EYEWASH ACTIVATION ALARM 36004 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2220 | 2 | 0001 | SH-46001 | SHA-46001F |  | SHOWER/EYEWASH ACTIVATION ALARM 46001 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2221 | 2 | 0001 | SH-46002 | SHA-46002F |  | SHOWER/EYEWASH ACTIVATION ALARM 46002 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND76 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 72
2222 | 4 | 0001 | SH-46003 | SHA-46003F |  | SHOWER/EYEWASH ACTIVATION ALARM 46003 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2223 | 4 | 0001 | SH-46004 | SHA-46004F |  | SHOWER/EYEWASH ACTIVATION ALARM 46004 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND77 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | Changed from 73
2224 | 3 | 0001 | SD-3000 | SA-3000F | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND74 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2225 | 3 | 0001 | TGD-3000 | TGA-3000F |  |  | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 |  |  | FGDS | FCR |  | MPF | 3000CND74 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2226 | 4 | 0001 | EWSD-3000 | EWXL-3000F | FAULT SIGNAL | Fault status lamp EWSD Area 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MPF | 3000CND74 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD
2227 | 3 | 0001 | MCP-3000 | MCP-3000F |  | MANUAL CALL POINT STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FCR |  | MPF | 3000CND74 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD
2228 | 3 | 0001 | IRGD-3000 | IRGD-3000F | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MPF | 3000CND74 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD
2229 | 3 | 0001 | TGD-3000 | TGD-3000F | Toxic gas, Signal to FCR | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MPF | 3000CND74 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD
2230 | 4 | 0001 | CLA-3000 | CLXA-Y3003F |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2231 | 3 | 0001 | CLA-3000 | CSA-Y3000F |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2232 | 4 | 0001 | CLA-3000 | CLXA-Y3001F |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2233 | 4 | 0001 | CLA-3000 | CLXA-Y3002F |  | CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2234 | 4 | 0001 | CLA-3000 | CLXA-Y3000F |  | FAULT STATUS LAMP AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2235 | 3 | 0001 | CLA-3000 | YSA-Y3000F |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2236 | 3 | 0001 | CLA-3000 | WAL-Y3000F |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Finishing Room (FRR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | FRR |  | MPF | 3000CND74 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2237 | 4 | 0002 | TGD-6000 | TGA-6000P | Toxic gas, Signal to PCR | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 6000 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2238 | 3 | 0002 | DV-12002 | HS-12702P |  | HAND SWITCH(PREPARATION CONTROL ROOM) 12002 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-PID-1912 | DIR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 4 | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39-4 | SYS/24Vdc | OPEN | [12 empty] | Line Monitoring
2239 | 4 | 0002 | MCP-12000 | MCP-12000P |  | MANUAL CALL POINT STATUS LAMP AREA 1200 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2240 | 4 | 0002 | IRGD-12000 | IRGA-12000P | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1200 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2241 | 4 | 0002 | FD-12000 | FAH-12000P | Fire and Gas, Signal to PCR | FIRE DETECTOR STATUS LAMP OF AREA 1200 | Signal to Matrix Panel Prepration Room (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2242 | 3 | 0002 | SH-12001 | SHA-12001P |  | SHOWER/EYEWASH ACTIVATION ALARM 12001 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2243 | 3 | 0002 | HVAC-6000 | MKHL-Y6000P |  | HVAC SHUTDOWN STATUS LAMP OF AREA 1200 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 1200CND70 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2244 | 3 | 0002 | SH-12002 | SHA-12002P |  | SHOWER/EYEWASH ACTIVATION ALARM 12002 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2245 | 3 | 0002 | HS-6070 | HS-6070P | General Alarm sounder Matrix Panel Prepration | Hand switch | Hand Switch | ESBR-HS-CAF-0006 | DIR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2246 | 4 | 0002 | SH-12003 | SHA-12003P |  | SHOWER/EYEWASH ACTIVATION ALARM 12003 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2247 | 3 | 0002 | UK-1070 | UK-6070P | Buzare Matrix Panel Prepration | Buzzer | Buzare | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2248 | 4 | 0002 | SH-12004 | SHA-12004P |  | SHOWER/EYEWASH ACTIVATION ALARM 12004 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND73 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2249 | 3 | 0002 | UK-6070 | HS-6071P | Acknowlege | Hand switch | Matrix Panel Hand switch(PCR) | ESBR-HS-CAF-0006 | DI | NIS | FGDS | PCR |  | MPP | 6000CND71 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
2250 | 3 | 0002 | UL-6070 | UL-6070AP | Prepration Room | General Falshing light on Matrix Panel | (YELLOW FLASHING LIGHT) Matrix Panel | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2251 | 3 | 0002 | UL-6070 | UL-6070BP | Prepration Room | General Falshing light on Matrix Panel | (RED FLASHING LIGHT) Matrix Panel | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2252 | 3 | 0002 | UL-6070 | UL-6070CP | Prepration Room | General Falshing light on Matrix Panel | (GREEN FLASHING LIGHT) Matrix Panel | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2253 | 3 | 0002 | DV-12002 | PAL-12702BP |  |  | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2254 | 3 | 0002 | DV-12002 | PAH-12702AP |  |  | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND71 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2255 | 2 | 0002 | SH-12005 | SHA-12005P |  | SHOWER/EYEWASH ACTIVATION ALARM 12005 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2256 | 2 | 0002 | SH-12006 | SHA-12006P |  | SHOWER/EYEWASH ACTIVATION ALARM 12006 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2257 | 2 | 0002 | SH-12007 | SHA-12007P |  | SHOWER/EYEWASH ACTIVATION ALARM 12007 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2258 | 2 | 0002 | SH-12008 | SHA-12008P |  | SHOWER/EYEWASH ACTIVATION ALARM 12008 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2259 | 2 | 0002 | SH-12009 | SHA-12009P |  | SHOWER/EYEWASH ACTIVATION ALARM 12009 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2260 | 2 | 0002 | SH-12010 | SHA-12010P |  | SHOWER/EYEWASH ACTIVATION ALARM 12010 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2261 | 2 | 0002 | SH-12011 | SHA-12011P |  | SHOWER/EYEWASH ACTIVATION ALARM 12011 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2262 | 2 | 0002 | SH-12012 | SHA-12012P |  | SHOWER/EYEWASH ACTIVATION ALARM 12012 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2263 | 2 | 0002 | SH-12013 | SHA-12013P |  | SHOWER/EYEWASH ACTIVATION ALARM 12013 | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | PCR |  | MPP | 6000CND72 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | CLOSE
2264 | 3 | 0000 | MCP-2000 | MCP-2000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2265 | 1 | 0003 | MCP-2000 | MCP-2000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2266 | 3 | 0000 | IRGD-2000 | IRGA-2000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 2000, Inclusive of HGD | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2267 | 1 | 0003 | IRGD-2000 | IRGA-2000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 2000 ,Iinclusive of HGD | Signal to GFAP In Fire station | ESBR-HS-CAS-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2268 | 2 | 0000 | IRGD-3000 | IRGA-3000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2269 | 2 | 0003 | IRGD-3000 | IRGA-3000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2270 | 2 | 0000 | TGD-3000 | TGA-3000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2271 | 2 | 0003 | TGD-3000 | TGA-3000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2272 | 3 | 0000 | FD-2000 | FAH-2000B | Fire and Gas, signal to CCR | FIRE DETECTOR STATUS LAMP OF MCC | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2273 | 1 | 0003 | FD-2000 | FA-2000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2274 | 3 | 0000 | SD-2000 | SA-2000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2275 | 1 | 0003 | SD-2000 | SA-2000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2276 | 3 | 0000 | TGD-2000 | TGA-2000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2277 | 1 | 0003 | TGD-2000 | TGA-2000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2278 | 3 | 0000 | EWSD-2000 | XL-2000B | FAULT SIGNAL | Fault status lamp EWSD Area 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND20 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2279 | 2 | 0003 | EWSD-2000 | XL-2000C | FAULT SIGNAL | Fault status lamp EWSD Area 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2280 | 3 | 0000 | EWSD-3000 | XL-3000B | FAULT SIGNAL | Fault status lamp EWSD Area 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2281 | 3 | 0003 | EWSD-3000 | XL-3000C | FAULT SIGNAL | Fault status lamp EWSD Area 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2282 | 3 | 0000 | HGD-2000 | HGA-2000B | Flammable gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 |  |  | FGDS | CRR |  | MP | 1000CND20 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2283 | 2 | 0003 | HGD-2000 | HGA-2000C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 |  |  | FGDS | CRR |  | GFAP | N.A
2284 | 3 | 0000 | IRGD-1000 | IRGA-1000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 1000, Inclusive of HGD | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2285 | 1 | 0003 | IRGD-1000 | IRGA-1000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 1000 ,Iinclusive of HGD | Signal to GFAP In Fire station | ESBR-HS-CAS-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2286 | 3 | 0000 | HGD-1000 | HGA-1000B | Fire and Gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0004 |  |  | FGDS | CRR |  | MP | 1000CND20 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2287 | 2 | 0003 | HGD-1000 | HGA-1000C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAS-0004 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2288 | 3 | 0000 | FD-1000 | FA-1000B | Fire and Gas, signal to CCR | FIRE GAS STATUS LAMP OF CCR | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0004 |  |  | FGDS | CRR |  | MP | 1000CND20 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2289 | 1 | 0003 | FD-1000 | FA-1000C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAS-0004 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2290 | 3 | 0000 | SD-1000 | SA-1000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2291 | 1 | 0003 | SD-1000 | SA-1000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2292 | 3 | 0000 | EWSD-1000 | XL-1000B | FAULT SIGNAL | Fault status lamp EWSD Area 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2293 | 2 | 0003 | EWSD-1000 | XL-1000C | FAULT SIGNAL | Fault status lamp EWSD Area 1000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2294 | 3 | 0000 | TGD-1000 | TGA-1000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2295 | 1 | 0003 | TGD-1000 | TGA-1000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2296 | 1 | 0000 | MCP-1000 | MCP-1000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2297 | 1 | 0003 | MCP-1000 | MCP-1000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2298 | 1 | 0000 | SD-3000 | SA-3000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2299 | 1 | 0003 | SD-3000 | SA-3000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2300 | 1 | 0000 | TGD-3000 | TGA-3000B | Toxic gas, Signal to CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 |  |  | FGDS | CRR |  | MP | 1000CND21 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2301 | 1 | 0003 | TGD-3000 | TGA-3000C | Signal connection through remote I/O |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2302 | 1 | 0000 | MCP-3000 | MCP-3000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2303 | 1 | 0003 | MCP-3000 | MCP-3000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2304 | 1 | 0000 | FD-4000 | FAH-4000B | Fire and Gas, signal to CCR | FIRE DETECTOR STATUS LAMP OF MAIN WORKSHOP | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2305 | 1 | 0003 | FD-4000 | FA-4000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 4000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2306 | 1 | 0000 | SD-4000 | SA-4000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 4000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2307 | 1 | 0003 | SD-4000 | SA-4000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 4000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2308 | 1 | 0000 | TGD-4000 | TGA-4000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 4000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2309 | 1 | 0003 | TGD-4000 | TGA-4000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 4000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2310 | 1 | 0000 | MCP-4000 | MCP-4000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 4000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2311 | 1 | 0003 | MCP-4000 | MCP-4000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 4000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2312 | 1 | 0000 | IRGD-4000 | IRGA-4000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 4000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2313 | 1 | 0003 | IRGD-4000 | IRGA-4000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 4000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2314 | 1 | 0000 | SD-5000 | SA-5000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2315 | 1 | 0003 | SD-5000 | SA-5000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 5000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2316 | 1 | 0000 | TGD-5000 | TGA-5000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2317 | 1 | 0003 | TGD-5000 | TGA-5000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 5000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2318 | 1 | 0000 | MCP-5000 | MCP-5000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2319 | 1 | 0003 | MCP-5000 | MCP-5000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 5000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2320 | 1 | 0000 | IRGD-5000 | IRGA-5000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2321 | 1 | 0003 | IRGD-5000 | IRGA-5000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 5000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2322 | 3 | 0000 | SD-6000 | SA-6000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 6000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | MP | 1000CND30 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2323 | 3 | 0000 | PSH-5750 | PSH-5750B | Pressure signal high for warehouse sprinkler system | FIRE DETECTOR STATUS LAMP OF AREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAS-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND21 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2324 | 3 | 0003 | PSH-5750 | PSH-5750C | Pressure signal high for warehouse sprinkler system | FIRE DETECTOR STATUS LAMP OF AREA 5000 | Signal to GFAP In Fire station | ESBR-HS-CAS-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2325 | 3 | 0000 | MCP-6000 | MCP-6000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 6000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | PCR |  | MP | 1000CND30 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2326 | 3 | 0003 | MCP-6000 | MCP-6000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 6000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2327 | 1 | 0003 | SD-6001 | SA-6000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 6000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2328 | 4 | 0000 | CLA-2000 | CLXA-Y2003B |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2329 | 3 | 0000 | CLA-2000 | CSA-Y2000B |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2330 | 4 | 0000 | CLA-2000 | CLXA-Y2001B |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2331 | 4 | 0000 | CLA-2000 | CLXA-Y2002B |  | OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2332 | 4 | 0000 | CLA-2000 | CLXA-Y2000B |  | FAULT STATUS LAMP Area 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2333 | 3 | 0000 | CLA-2000 | YSA-Y2000B |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2334 | 3 | 0000 | CLA-2000 | WAL-Y2000B |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2335 | 4 | 0000 | CLA-1000 | CLXA-Y1003B |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2336 | 3 | 0000 | CLA-1000 | CSA-Y1000B |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2337 | 4 | 0000 | CLA-1000 | CLXA-Y1001B |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2338 | 4 | 0000 | CLA-1000 | CLXA-Y1002B |  | CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2339 | 4 | 0000 | CLA-1000 | CLXA-Y1000B |  | FAULT STATUS LAMP AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2340 | 3 | 0000 | CLA-1000 | YSA-Y1000B |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2341 | 3 | 0000 | CLA-1000 | WAL-Y1000B |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OFAREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND22 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2342 | 4 | 0000 | CLA-3000 | CLXA-Y3003B |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2343 | 3 | 0000 | CLA-3000 | CSA-Y3000B |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2344 | 4 | 0000 | CLA-3000 | CLXA-Y3001B |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2345 | 4 | 0000 | CLA-3000 | CLXA-Y3002B |  | CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2346 | 4 | 0000 | CLA-3000 | CLXA-Y3000B |  | FAULT STATUS LAMP AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2347 | 3 | 0000 | CLA-3000 | YSA-Y3000B |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2348 | 3 | 0000 | CLA-3000 | WAL-Y3000B |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2349 | 4 | 0003 | CLA-2000 | CLXA-Y2003C |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2350 | 2 | 0003 | CLA-2000 | CSA-Y2000C |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2351 | 4 | 0003 | CLA-2000 | CLXA-Y2001C |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2352 | 4 | 0003 | CLA-2000 | CLXA-Y2002C |  | OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2353 | 4 | 0003 | CLA-2000 | CLXA-Y2000C |  | FAULT STATUS LAMP Area 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2354 | 2 | 0003 | CLA-2000 | YSA-Y2000C |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2355 | 2 | 0003 | CLA-2000 | WAL-Y2000C |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2356 | 4 | 0003 | CLA-1000 | CLXA-Y1003C |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2357 | 2 | 0003 | CLA-1000 | CSA-Y1000C |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2358 | 4 | 0003 | CLA-1000 | CLXA-Y1001C |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2359 | 4 | 0003 | CLA-1000 | CLXA-Y1002C |  | CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2360 | 4 | 0003 | CLA-1000 | CLXA-Y1000C |  | FAULT STATUS LAMP AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2361 | 2 | 0003 | CLA-1000 | YSA-Y1000C |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2362 | 2 | 0003 | CLA-1000 | WAL-Y1000C |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OFAREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2363 | 4 | 0003 | CLA-3000 | CLXA-Y3003C |  | CLEAN AGENT ACTIVATION STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2364 | 2 | 0003 | CLA-3000 | CSA-Y3000C |  | CLEAN AGENT INHIBIT STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2365 | 4 | 0003 | CLA-3000 | CLXA-Y3001C |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2366 | 4 | 0003 | CLA-3000 | CLXA-Y3002C |  | CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF Area 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2367 | 4 | 0003 | CLA-3000 | CLXA-Y3000C |  | FAULT STATUS LAMP AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2368 | 2 | 0003 | CLA-3000 | YSA-Y3000C |  | LOCK OFF VALVE CLOSED STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2369 | 2 | 0003 | CLA-3000 | WAL-Y3000C |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE | [12 empty] | ON HOLD, Subject to vendor data
2370 | 2 | 0000 | HVAC-1000 | MKHL-Y1000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 1000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0004 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2371 | 2 | 0000 | HVAC-2000 | MKHL-Y2000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 2000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0003 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2372 | 2 | 0000 | HVAC-3000 | MKHL-Y3000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 3000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0005 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2373 | 2 | 0000 | HVAC-4000 | MKHL-Y4000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 4000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0007 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2374 | 2 | 0000 | HVAC-5000 | MKHL-Y5000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 5000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0008 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2375 | 3 | 0000 | HVAC-6000 | MKHL-Y6000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 1200 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0006 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2376 | 3 | 0000 | HVAC-7000 | MKHL-Y7000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 7000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0009 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2377 | 3 | 0000 | HVAC-8000 | MKHL-Y8000B |  | HVAC SHUTDOWN STATUS LAMP OF AREA 8000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0010 | DOR | NIS | FGDS | CRR |  | MP | 1000CND31 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2378 | 2 | 0003 | HVAC-1000 | MKHL-Y1000C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 1000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2379 | 2 | 0003 | HVAC-2000 | MKHL-Y2000C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 2000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2380 | 2 | 0003 | HVAC-3000 | MKHL-Y3000C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 3000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2381 | 2 | 0003 | HVAC-4000 | MKHL-Y4000C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 4000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2382 | 2 | 0003 | HVAC-5000 | MKHL-Y5000C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 5000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2383 | 3 | 0003 | HVAC-1200 | MKHL-Y1200C |  | HVAC SHUTDOWN STATUS LAMP OF AREA 1200 | Signal to GFAP In Fire station | ESBR-HS-CAF-0006 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2384 | 3 | 0003 | HVAC-7000 | MKHL-Y7000 |  | HVAC SHUTDOWN STATUS LAMP OF AREA 7000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2385 | 3 | 0003 | HVAC-8000 | MKHL-Y8000 |  | HVAC SHUTDOWN STATUS LAMP OF AREA 8000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2386 | 3 | 2000 | HVAC-2000 | HVAC-2000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2387 | 3 | 1000 | HVAC-1000 | HVAC-1000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2388 | 4 | 3000 | CLA-3000 | CLXA-Y3003A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2389 | 3 | 4000 | HVAC-4000 | HVAC-4000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2390 | 3 | 4000 | HVAC-4000 | HVAC-4002 | HVAC status |  | HVAC signals to FGS |  |  |  | FGDS | CRR |  | LFAP | CAP-4000 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2391 | 3 | 5000 | HVAC-5000 | HVAC-5000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2392 | 3 | 7000 | HVAC-7000 | HVAC-7000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0009 | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-8
2393 | 3 | 8000 | HVAC-8000 | HVAC-8000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0010 | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-8
2394 | 1 | 2000 | MCP-2000 | MCP-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2395 | 1 | 2000 | IRGD-2000 | IRGA-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2396 | 1 | 2000 | SD-2000 | SA-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2397 | 1 | 2000 | TGD-2000 | TGA-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2398 | 1 | 2000 | HGD-2000 | HGA-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2399 | 2 | 2000 | FD-2000 | FA-2000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0003
2400 | 1 | 2000 | EWSD-2000 | EWSA-2000 | Alarm from FAP to FGS | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2401 | 2 | 2000 | EWSD-2000 | XL-2000 | Fault Signal | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2
2402 | 4 | 2000 | CLA-2000 | CLXA-Y2003A | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2403 | 2 | 2000 | CLA-2000 | CSA-Y2000A | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2404 | 4 | 2000 | CLA-2000 | CLXA-Y2001A | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2405 | 4 | 2000 | CLA-2000 | CLXA-Y2002A | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2406 | 4 | 2000 | CLA-2000 | CLXA-Y2000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Subject to vendor data
2407 | 2 | 2000 | CLA-2000 | YSA-Y2000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2408 | 2 | 2000 | CLA-2000 | WAL-Y2000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DI | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4 |  |  |  | ON HOLD, Subject to vendor data
2409 | 1 | 1000 | IRGD-1000 | IRGA-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2410 | 1 | 1000 | FD-1000 | FA-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS |  |  |  | FGDS | CRR |  | LFAP | CAP-1000A |  | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2411 | 1 | 1000 | SD-1000 | SA-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2412 | 1 | 1000 | TGD-1000 | TGA-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2413 | 1 | 1000 | MCP-1000 | MCP-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2414 | 2 | 1000 | HGD-1000 | HGA-1000 | Status signal from LFAP |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-2
2415 | 1 | 1000 | EWSD-1000 | EWSA-1000 | Alarm from FAP to FGS | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2416 | 2 | 1000 | EWSD-1000 | XL-1000 | Fault Signal | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2417 | 4 | 1000 | CLA-1000 | CLXA-Y1003A | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2418 | 4 | 1000 | CLA-1000 | CSA-Y1000A | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2419 | 4 | 1000 | CLA-1000 | CLXA-Y1001A | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2420 | 4 | 1000 | CLA-1000 | CLXA-Y1002A | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2421 | 4 | 1000 | CLA-1000 | CLXA-Y1000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2422 | 4 | 1000 | CLA-1000 | YSA-Y1000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2423 | 4 | 1000 | CLA-1000 | WAL-Y1000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2424 | 4 | 3000 | CLA-3000 | CSA-Y3000A | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2425 | 4 | 3000 | CLA-3000 | CLXA-Y3001A | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2426 | 4 | 3000 | CLA-3000 | CLXA-Y3002A | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  |  |  | ON HOLD, Subject to vendor data
2427 | 1 | 3000 | EWSD-3000 | EWSA-3000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2428 | 2 | 3000 | EWSD-3000 | XL-3000 | Alarm from FAP to FGS | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2429 | 2 | 3000 | HVAC-3000 | HVAC-3000A | Fault Signal | On Hold | Status signal From FAP TO FGS | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2430 | 2 | 3000 | IRGD-3000 | IRGA-3000 | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2431 | 2 | 3000 | SD-3000 | SA-3000 | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2432 | 2 | 3000 | TGD-3000 | TGA-3000 | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2433 | 2 | 3000 | MCP-3000 | MCP-3000 | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2434 | 4 | 3000 | CLA-3000 | CLXA-Y3000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2435 | 4 | 3000 | CLA-3000 | YSA-Y3000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2436 | 4 | 3000 | CLA-3000 | WAL-Y3000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DI | NIS | FGDS | FRR |  | LFAP | CAP-3000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3 |  |  |  | ON HOLD, Subject to vendor data
2437 | 3 | 4000 | FD-4000 | FA-4000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2438 | 3 | 4000 | SD-4000 | SA-4000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2439 | 3 | 4000 | TGD-4000 | TGA-4000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2440 | 3 | 4000 | MCP-4000 | MCP-4000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2441 | 3 | 4000 | IRGD-4000 | IRGA-4000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2442 | 3 | 5000 | SD-5000 | SA-5000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2443 | 3 | 5000 | PSH-5750 | PSH-5750A | Status signal to FGS |  | Pressure signal high for warehouse sprinkler system | ESBR-HS-PID-0004 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 16 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
2444 | 3 | 5000 | TGD-5000 | TGA-5000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2445 | 3 | 5000 | MCP-5000 | MCP-5000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2446 | 3 | 5000 | IRGD-5000 | IRGA-5000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2447 | 3 | 5000 | SDOP-5000 | SAOP-5000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0008 | DI | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2448 | 4 | 2000 | LFAP-2000 | LFXF-2000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2449 | 4 | 2000 | LFAP-2000 | LFXA-2000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2450 | 4 | 1000 | LFAP-1000 | LFXF-1000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2451 | 4 | 1000 | LFAP-1000 | LFXA-1000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1
2452 | 4 | 3000 | LFAP-3000 | LFXF-3000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2453 | 4 | 3000 | LFAP-3000 | LFXA-3000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-3
2454 | 4 | 4000 | LFAP-4000 | LFXF-4000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2455 | 4 | 4000 | LFAP-4000 | LFXA-4000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-4
2456 | 4 | 5000 | LFAP-5000 | LFXF-5000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2457 | 4 | 5000 | LFAP-5000 | LFXA-5000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-5
2458 | 4 | 7000 | LFAP-7000 | LFXF-7000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-6
2459 | 4 | 7000 | LFAP-7000 | LFXA-7000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-6
2460 | 4 | 8000 | LFAP-8000 | LFXF-8000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-7
2461 | 4 | 8000 | LFAP-8000 | LFXA-8000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DIR | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-7
2462 | 3 | 5000 | HVAC-5000 | XL-Y5000 | HVAC status |  | HVAC signals to FGS |  |  |  | FGDS |  |  | LFAP | CAP-5000 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-1 |  | ESBR-CI-DAS-0030
2463 | 2 | 2000 | UK-2000 | UK-2000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2464 | 2 | 2000 | UK-2000 | UK-2000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2465 | 2 | 2000 | UK-2000 | UK-2000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2466 | 2 | 2000 | UL-2000 | UL-2000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2467 | 2 | 2000 | UL-2000 | UL-2000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2468 | 2 | 2000 | UL-2000 | UL-2000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2469 | 2 | 1000 | UK-1000 | UK-1000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2470 | 2 | 1000 | UK-1000 | UK-1000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2471 | 2 | 1000 | UK-1000 | UK-1000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2472 | 2 | 1000 | UL-1000 | UL-1000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2473 | 2 | 1000 | UL-1000 | UL-1000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2474 | 2 | 1000 | UL-1000 | UL-1000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2475 | 2 | 3000 | UK-3000 | UK-3000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2476 | 2 | 3000 | UK-3000 | UK-3000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2477 | 2 | 3000 | UK-3000 | UK-3000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2478 | 2 | 3000 | UL-3000 | UL-3000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2479 | 2 | 3000 | UL-3000 | UL-3000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2480 | 2 | 3000 | UL-3000 | UL-3000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2481 | 3 | 4000 | UK-4000 | UK-4000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2482 | 3 | 4000 | UK-4000 | UK-4000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2483 | 3 | 4000 | UK-4000 | UK-4000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2484 | 3 | 4000 | UL-4000 | UL-4000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2485 | 3 | 4000 | UL-4000 | UL-4000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2486 | 3 | 4000 | UL-4000 | UL-4000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 15 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2487 | 3 | 5000 | UK-5000 | UK-5000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2488 | 3 | 5000 | UK-5000 | UK-5000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2489 | 3 | 5000 | UK-5000 | UK-5000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2490 | 3 | 5000 | UL-5000 | UL-5000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2491 | 3 | 5000 | UL-5000 | UL-5000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2492 | 3 | 5000 | UL-5000 | UL-5000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2493 | 3 | 7000 | UK-7000 | UK-7000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2494 | 3 | 7000 | UK-7000 | UK-7000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2495 | 3 | 7000 | UK-7000 | UK-7000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2496 | 3 | 7000 | UL-7000 | UL-7000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2497 | 3 | 7000 | UL-7000 | UL-7000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2498 | 3 | 7000 | UL-7000 | UL-7000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2499 | 3 | 8000 | UK-8000 | UK-8000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2500 | 3 | 8000 | UK-8000 | UK-8000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2501 | 3 | 8000 | UK-8000 | UK-8000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2502 | 3 | 8000 | UL-8000 | UL-8000A | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2503 | 3 | 8000 | UL-8000 | UL-8000B | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2504 | 3 | 8000 | UL-8000 | UL-8000C | Signal to LFAP |  | Activation alarm from F&G |  | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | CLOSE
2505 | 2 | 1100 | FM-01 | UV-11751 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2506 | 4 | 1100 | FM-01 | HY-11751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP01 | 1 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1101 |  |  |  | Signal connection is seen through a use of Solenoid,
2507 | 4 | 1100 | FM-01 | ZSL-11751 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP01 | 2 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1101 |  |  |  | Replaced by 1100JNS93
2508 | 4 | 1100 | FM-01 | ZSH-11751 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP01 | 3 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1101
2509 | 3 | 0000 | FM-01 | ZAH-11751B | Valve open alarm at CCR | Valve open alarm at CCR FM-01 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2510 | 2 | 0003 | FM-01 | ZAH-11751C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-01 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2511 | 3 | 0000 | FM-01 | HS-11751B | Remote open from Matrix Panel | Hand switch Control room FM-01 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 2 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2512 | 4 | 0000 | FM-01 | XS-11751LB |  | Hand switch Lamp Control room FM-01 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2513 | 2 | 0002 | FM-01 | HS-11751P | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 |  |  | FGDS | PCR |  | MPP | 6000CND72 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2514 | 4 | 1100 | FM-01 | HS-11751 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 | [6 empty] | LCP01 | 4 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2515 | 2 | 1100 | FM-01 | ZAH-11751 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2516 | 2 | 1100 | FM-01 | ZAL-11751 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2517 | 2 | 1100 | FM-01 | MR-11751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  |  | Open
2518 | 2 | 1200 | FM-02 | UV-12752 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Signal connection is seen through a use of Solenoid
2519 | 2 | 1200 | FM-02 | HY-12752 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 1200JNS91 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2520 | 2 | 1200 | FM-02 | ZSL-12752 | Valve Close | [5 empty] | FGDS | CRR | d | F | 1200JNS90 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2521 | 2 | 1200 | FM-02 | ZSH-12752 | Valve open | [5 empty] | FGDS | CRR | d | F | 1200JNS90 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2522 | 3 | 0000 | FM-02 | ZAH-12752B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND24 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2523 | 2 | 0003 | FM-02 | ZAH-12752C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2524 | 3 | 0000 | FM-02 | HS-12752B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND24 |  | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2525 | 2 | 0002 | FM-01 | HS-12752P | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel PreprationRoom (PRR) | ESBR-HS-CAF-0002 |  |  | FGDS | PCR |  | MPP | 6000CND72 |  | 16-P-1.50-11-SWA-S-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2526 | 2 | 1200 | FM-02 | HS-12752A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2527 | 2 | 1200 | FM-02 | ZAH-12752 | Alarm valve Open
2528 | 2 | 1200 | FM-02 | ZAL-12752 | Alarm valve Close
2529 | 2 | 1200 | FM-02 | MR-12752 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2530 | 2 | 1300 | FM-03 | UV-13751 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2531 | 4 | 1300 | FM-03 | HY-13751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP02 | 1 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid,
2532 | 4 | 1300 | FM-03 | ZSL-13751 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP02 | 2 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2533 | 4 | 1300 | FM-03 | ZSH-13751 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP02 | 3 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced by 1300JNS95
2534 | 3 | 0000 | FM-03 | ZAH-13751B | Valve open alarm at CCR | Valve open alarm at CCR FM-03 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2535 | 2 | 0003 | FM-03 | ZAH-13751C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-03 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2536 | 4 | 0000 | FM-03 | HS-13751B | Remote open from Matrix Panel | Hand switch Control room FM-03 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 4 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2537 | 4 | 0000 | FM-03 | XS-13751LB |  | Hand switch Lamp Control room FM-03 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2538 | 3 | 1300 | FM-03 | HS-13751 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 | [6 empty] | LCP02 | 4 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2539 | 2 | 1300 | FM-03 | ZAH-13751 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2540 | 2 | 1300 | FM-03 | ZAL-13751 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2541 | 2 | 1300 | FM-03 | MR-13751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2542 | 2 | 1300 | FM-04 | UV-13752 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2543 | 4 | 1300 | FM-04 | HY-13752 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP02 | 5 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid,
2544 | 4 | 1300 | FM-04 | ZSL-13752 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP02 | 6 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced by 1300JNS96
2545 | 4 | 1300 | FM-04 | ZSH-13752 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP02 | 7 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2546 | 3 | 0000 | FM-04 | ZAH-13752B | Valve open alarm at CCR | Valve open alarm at CCR FM-04 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2547 | 2 | 0003 | FM-04 | ZAH-13752C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-04 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2548 | 3 | 0000 | FM-04 | HS-13752B | Remote open from Matrix Panel | Hand switch Control room FM-04 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 6 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2549 | 4 | 0000 | FM-04 | XS-13752LB |  | Hand switch Lamp Control room FM-04 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2550 | 4 | 1300 | FM-04 | HS-13752 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 | [6 empty] | LCP02 | 8 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2551 | 2 | 1300 | FM-04 | ZAH-13752 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2552 | 2 | 1300 | FM-04 | ZAL-13752 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2553 | 2 | 1300 | FM-04 | MR-13752 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2554 | 3 | 1400 | FM-14 | UV-14754A | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2555 | 3 | 1400 | FM-14 | UV-14754B | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2556 | 3 | 1400 | FM-14 | UV-14754C | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2557 | 4 | 1400 | FM-14 | HY-14754A | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 6 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2558 | 4 | 1400 | FM-14 | HY-14754B | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 7 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2559 | 4 | 1400 | FM-14 | HY-14754C | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 8 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2560 | 4 | 1400 | FM-14 | ZSL-14754A | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 9 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced by 1400JNS97
2561 | 4 | 1400 | FM-14 | ZSH-14754A | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 10 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2562 | 4 | 1400 | FM-14 | ZSL-14754B | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 11 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2563 | 4 | 1400 | FM-14 | ZSH-14754B | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 12 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2564 | 4 | 1400 | FM-14 | ZSL-14754C | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 13 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2565 | 4 | 1400 | FM-14 | ZSH-14754C | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 14 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2566 | 3 | 0000 | FM-14 | ZAH-14754AB | Valve open alarm at CCR | Valve open alarm at CCR FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2567 | 3 | 0000 | FM-14 | ZAH-14754BB | Valve open alarm at CCR | Valve open alarm at CCR FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2568 | 3 | 0000 | FM-14 | ZAH-14754CB | Valve open alarm at CCR | Valve open alarm at CCR FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND24 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2569 | 3 | 0003 | FM-14 | ZAH-14754AC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-14 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2570 | 3 | 0003 | FM-14 | ZAH-14754BC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-14 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2571 | 3 | 0003 | FM-14 | ZAH-14754CC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-14 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2572 | 3 | 0000 | FM-14 | HS-14754AB | Remote open from Matrix Panel | Hand switch Control room FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 10 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2573 | 4 | 0000 | FM-14 | XS-14754LAB |  | Hand switch Lamp Control room FM-14 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2574 | 3 | 0000 | FM-14 | HS-14754BB | Remote open from Matrix Panel | Hand switch Control room FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 11 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2575 | 4 | 0000 | FM-14 | XS-14754LBB |  | Hand switch Lamp Control room FM-14 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2576 | 3 | 0000 | FM-14 | HS-14754CB | Remote open from Matrix Panel | Hand switch Control room FM-14 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND24 | 12 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2577 | 4 | 0000 | FM-14 | XS-14754LCB |  | Hand switch Lamp Control room FM-14 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2578 | 4 | 1400 | FM-14 | HS-14754A | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 15 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2579 | 4 | 1400 | FM-14 | HS-14754B | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 16 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2580 | 4 | 1400 | FM-14 | HS-14754C | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 17 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2581 | 3 | 1400 | FM-14 | ZAH-14754A | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2582 | 3 | 1400 | FM-14 | ZAL-14754A | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2583 | 3 | 1400 | FM-14 | ZAH-14754B | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2584 | 3 | 1400 | FM-14 | ZAL-14754B | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2585 | 3 | 1400 | FM-14 | ZAH-14754C | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2586 | 3 | 1400 | FM-14 | ZAL-14754C | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2587 | 2 | 1400 | FM-14 | MR-14754 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2588 | 3 | 1400 | FM-15 | UV-14755A | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2589 | 3 | 1400 | FM-15 | UV-14755B | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2590 | 3 | 1400 | FM-15 | UV-14755C | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2591 | 4 | 1400 | FM-15 | HY-14755A | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 19 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2592 | 4 | 1400 | FM-15 | HY-14755B | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 20 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2593 | 4 | 1400 | FM-15 | HY-14755C | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 21 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2594 | 4 | 1400 | FM-15 | ZSL-14755A | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 22 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced by 1400JNS98
2595 | 4 | 1400 | FM-15 | ZSH-14755A | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 23 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2596 | 4 | 1400 | FM-15 | ZSL-14755B | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 24 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2597 | 4 | 1400 | FM-15 | ZSH-14755B | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 25 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2598 | 4 | 1400 | FM-15 | ZSL-14755C | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 26 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2599 | 4 | 1400 | FM-15 | ZSH-14755C | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 27 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2600 | 3 | 0000 | FM-15 | ZAH-14755AB | Valve open alarm at CCR | Valve open alarm at CCR FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2601 | 3 | 0000 | FM-15 | ZAH-14755BB | Valve open alarm at CCR | Valve open alarm at CCR FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2602 | 3 | 0000 | FM-15 | ZAH-14755CB | Valve open alarm at CCR | Valve open alarm at CCR FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2603 | 3 | 0003 | FM-15 | ZAH-14755AC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-15 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2604 | 3 | 0003 | FM-15 | ZAH-14755BC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-15 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2605 | 3 | 0003 | FM-15 | ZAH-14755CC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-15 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2606 | 3 | 0000 | FM-15 | HS-14755AB | Remote open from Matrix Panel | Hand switch Control room FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 4 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2607 | 4 | 0000 | FM-15 | XS-14755LAB |  | Hand switch Lamp Control room FM-15 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2608 | 3 | 0000 | FM-15 | HS-14755BB | Remote open from Matrix Panel | Hand switch Control room FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 5 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2609 | 4 | 0000 | FM-15 | XS-14755LBB |  | Hand switch Lamp Control room FM-15 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2610 | 3 | 0000 | FM-15 | HS-14755CB | Remote open from Matrix Panel | Hand switch Control room FM-15 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 6 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2611 | 4 | 0000 | FM-15 | XS-14755LCB |  | Hand switch Lamp Control room FM-15 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2612 | 4 | 1400 | FM-15 | HS-14755A | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 28 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2613 | 4 | 1400 | FM-15 | HS-14755B | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 29 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2614 | 4 | 1400 | FM-15 | HS-14755C | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 30 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2615 | 3 | 1400 | FM-15 | ZAH-14755A | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2616 | 3 | 1400 | FM-15 | ZAL-14755A | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2617 | 3 | 1400 | FM-15 | ZAH-14755B | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2618 | 3 | 1400 | FM-15 | ZAL-14755B | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2619 | 3 | 1400 | FM-15 | ZAH-14755C | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2620 | 3 | 1400 | FM-15 | ZAL-14755C | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2621 | 2 | 1400 | FM-15 | MR-14755 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2622 | 3 | 1400 | FM-16 | UV-14756A | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2623 | 3 | 1400 | FM-16 | UV-14756B | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2624 | 3 | 1400 | FM-16 | UV-14756C | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2625 | 4 | 1400 | FM-16 | HY-14756A | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP04 | 11 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2626 | 4 | 1400 | FM-16 | HY-14756B | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP04 | 12 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2627 | 4 | 1400 | FM-16 | HY-14756C | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP04 | 13 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Signal connection is seen through a use of Solenoid
2628 | 4 | 1400 | FM-16 | ZSL-14756A | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 14 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301 |  |  |  | Replaced by 1400JNS99
2629 | 4 | 1400 | FM-16 | ZSH-14756A | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 15 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2630 | 4 | 1400 | FM-16 | ZSL-14756B | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 16 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2631 | 4 | 1400 | FM-16 | ZSH-14756B | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 17 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2632 | 4 | 1400 | FM-16 | ZSL-14756C | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 18 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2633 | 4 | 1400 | FM-16 | ZSH-14756C | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 19 | 16-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1301
2634 | 3 | 0000 | FM-16 | ZAH-14756AB | Valve open alarm at CCR | Valve open alarm at CCR FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2635 | 3 | 0000 | FM-16 | ZAH-14756BB | Valve open alarm at CCR | Valve open alarm at CCR FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2636 | 3 | 0000 | FM-16 | ZAH-14756CB | Valve open alarm at CCR | Valve open alarm at CCR FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2637 | 3 | 0003 | FM-16 | ZAH-14756AC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-16 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2638 | 3 | 0003 | FM-16 | ZAH-14756BC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-16 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2639 | 3 | 0003 | FM-16 | ZAH-14756CC | Valve open alarm at GFAP | Valve open alarm at GFAP FM-16 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2640 | 3 | 0000 | FM-16 | HS-14756AB | Remote open from Matrix Panel | Hand switch Control room FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 10 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2641 | 4 | 0000 | FM-16 | XS-14756LAB |  | Hand switch Lamp Control room FM-16 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2642 | 3 | 0000 | FM-16 | HS-14756BB | Remote open from Matrix Panel | Hand switch Control room FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 11 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2643 | 4 | 0000 | FM-16 | XS-14756LBB |  | Hand switch Lamp Control room FM-16 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2644 | 3 | 0000 | FM-16 | HS-14756CB | Remote open from Matrix Panel | Hand switch Control room FM-16 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 12 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2645 | 4 | 0000 | FM-16 | XS-14756LCB |  | Hand switch Lamp Control room FM-16 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2646 | 4 | 1400 | FM-16 | HS-14756A | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP04 | 20 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2647 | 4 | 1400 | FM-16 | HS-14756B | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP04 | 21 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2648 | 4 | 1400 | FM-16 | HS-14756C | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP04 | 22 | 16-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2649 | 3 | 1400 | FM-16 | ZAH-14756A | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2650 | 3 | 1400 | FM-16 | ZAL-14756A | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2651 | 3 | 1400 | FM-16 | ZAH-14756B | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2652 | 3 | 1400 | FM-16 | ZAL-14756B | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2653 | 3 | 1400 | FM-16 | ZAH-14756C | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2654 | 3 | 1400 | FM-16 | ZAL-14756C | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2655 | 2 | 2300 | FM-05 | UV-23751 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2656 | 4 | 2300 | FM-05 | HY-23751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP01 | 5 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Signal connection is seen through a use of Solenoid
2657 | 4 | 2300 | FM-05 | ZSL-23751 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP01 | 6 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-2301 |  |  |  | Replaced by 2300JNS95
2658 | 4 | 2300 | FM-05 | ZSH-23751 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP01 | 7 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-2301
2659 | 3 | 0000 | FM-05 | ZAH-23751B | Valve open alarm at CCR | Valve open alarm at CCR FM-05 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2660 | 2 | 0003 | FM-05 | ZAH-23751C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-05 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2661 | 3 | 0000 | FM-05 | HS-23751B | Remote open from Matrix Panel | Hand switch Control room FM-05 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 8 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2662 | 4 | 0000 | FM-05 | XS-23751LB |  | Hand switch Lamp Control room FM-05 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2663 | 4 | 2300 | FM-05 | HS-23751 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP01 | 8 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2664 | 2 | 2300 | FM-05 | ZAH-23751 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2665 | 2 | 2300 | FM-05 | ZAL-23751 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2666 | 2 | 2300 | FM-05 | MR-23751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2667 | 2 | 1400 | FM-06 | UV-14751 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2668 | 4 | 1400 | FM-06 | HY-14751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP03 | 1 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Signal connection is seen through a use of Solenoid
2669 | 4 | 1400 | FM-06 | ZSL-14751 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 2 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced by 1400JNS91
2670 | 4 | 1400 | FM-06 | ZSH-14751 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP03 | 3 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401
2671 | 3 | 0000 | FM-06 | ZAH-14751B | Valve open alarm at CCR | Valve open alarm at CCR FM-06 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2672 | 2 | 0003 | FM-06 | ZAH-14751C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-06 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2673 | 3 | 0000 | FM-06 | HS-14751B | Remote open from Matrix Panel | Hand switch Control room FM-06 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 10 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2674 | 4 | 0000 | FM-06 | XS-14751LB |  | Hand switch Lamp Control room FM-06 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2675 | 4 | 1400 | FM-06 | HS-14751 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP03 | 4 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2676 | 2 | 1400 | FM-06 | ZAH-14751 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2677 | 2 | 1400 | FM-06 | ZAL-14751 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2678 | 2 | 1400 | FM-06 | MR-14751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2679 | 2 | 1400 | FM-07 | UV-14752 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2680 | 4 | 1400 | FM-07 | HY-14752 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP04 | 1 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Signal connection is seen through a use of Solenoid
2681 | 4 | 1400 | FM-07 | ZSL-14752 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 2 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced by 1400JNS92
2682 | 4 | 1400 | FM-07 | ZSH-14752 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 3 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401
2683 | 3 | 0000 | FM-07 | ZAH-14752B | Valve open alarm at CCR | Valve open alarm at CCR FM-07 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND25 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2684 | 2 | 0003 | FM-07 | ZAH-14752C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-07 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2685 | 3 | 0000 | FM-07 | HS-14752B | Remote open from Matrix Panel | Hand switch Control room FM-07 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND25 | 12 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2686 | 4 | 0000 | FM-07 | XS-14752LB |  | Hand switch Lamp Control room FM-07 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2687 | 4 | 1400 | FM-07 | HS-14752 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP04 | 4 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2688 | 2 | 1400 | FM-07 | ZAH-14752 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2689 | 2 | 1400 | FM-07 | ZAL-14752 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2690 | 2 | 1400 | FM-07 | MR-14752 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2691 | 2 | 1400 | FM-13 | UV-14753 | Fire water Monitor Remote Control Elevated |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2692 | 4 | 1400 | FM-13 | HY-14753 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP04 | 6 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Signal connection is seen through a use of Solenoid
2693 | 4 | 1400 | FM-13 | ZSL-14753 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 7 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401 |  |  |  | Replaced by 1400JNS94
2694 | 4 | 1400 | FM-13 | ZSH-14753 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP04 | 8 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-1401
2695 | 3 | 0000 | FM-13 | ZAH-14753B | Valve open alarm at CCR | Valve open alarm at CCR FM-13 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2696 | 2 | 0003 | FM-13 | ZAH-14753C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-13 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2697 | 3 | 0000 | FM-13 | HS-14753B | Remote open from Matrix Panel | Hand switch Control room FM-13 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 2 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2698 | 4 | 0000 | FM-13 | XS-14753LB |  | Hand switch Lamp Control room FM-13 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2699 | 4 | 1400 | FM-13 | HS-14753 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP04 | 9 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2700 | 2 | 1400 | FM-13 | ZAH-14753 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2701 | 2 | 1400 | FM-13 | ZAL-14753 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2702 | 2 | 1400 | FM-13 | MR-14753 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2703 | 2 | 1100 | WF-01 | UV-11751 | Fire water Monitor , Water Foam |  |  | ESBR-HS-PID-0016
2704 | 2 | 1100 | WF-01 | HY-11751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 1100JNS93 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2705 | 2 | 1100 | WF-01 | ZSL-11751 | Valve Close |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS93 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2706 | 2 | 1100 | WF-01 | ZSH-11751 | Valve open |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS93 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2707 | 3 | 0000 | WF-01 | ZAH-11751B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2708 | 2 | 0003 | WF-01 | ZAH-11751C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2709 | 3 | 0000 | WF-01 | HS-11751B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2710 | 2 | 1100 | WF-01 | HS-11751A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2711 | 2 | 1100 | WF-01 | ZAH-11751 | Alarm valve Open
2712 | 2 | 1100 | WF-01 | ZAL-11751 | Alarm valve Close
2713 | 2 | 1100 | WF-01 | MR-11751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2714 | 2 | 1100 | WF-02 | UV-11752 | Fire water Monitor , Water Foam |  |  | ESBR-HS-PID-0016
2715 | 2 | 1100 | WF-02 | HY-11752 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 1100JNS94 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2716 | 2 | 1100 | WF-02 | ZSL-11752 | Valve Close |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS94 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2717 | 2 | 1100 | WF-02 | ZSH-11752 | Valve open |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS94 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2718 | 3 | 0000 | WF-02 | ZAH-11752B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2719 | 2 | 0003 | WF-02 | ZAH-11752C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2720 | 3 | 0000 | WF-02 | HS-11752B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2721 | 2 | 1100 | WF-02 | HS-11752A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2722 | 2 | 1100 | WF-02 | ZAH-11752 | Alarm valve Open
2723 | 2 | 1100 | WF-02 | ZAL-11752 | Alarm valve Close
2724 | 2 | 1100 | WF-02 | MR-11752 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2725 | 2 | 1100 | WF-03 | UV-11753 | Fire water Monitor , Water Foam |  |  | ESBR-HS-PID-0016
2726 | 2 | 1100 | WF-03 | HY-11753 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 1100JNS95 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2727 | 2 | 1100 | WF-03 | ZSL-11753 | Valve Close |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS95 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2728 | 2 | 1100 | WF-03 | ZSH-11753 | Valve open |  |  | ESBR-HS-PID-0016 |  |  | FGDS | CRR | d | F | 1100JNS95 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2729 | 3 | 0000 | WF-03 | ZAH-11753B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2730 | 2 | 0003 | WF-03 | ZAH-11753C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2731 | 3 | 0000 | WF-03 | HS-11753B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2732 | 2 | 1100 | WF-03 | HS-11753A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2733 | 2 | 1100 | WF-03 | ZAH-11753 | Alarm valve Open
2734 | 2 | 1100 | WF-03 | ZAL-11753 | Alarm valve Close
2735 | 2 | 1100 | WF-03 | MR-11753 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2736 | 2 | 2100 | FM-08 | UV-11754 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Signal connection is seen through a use of Solenoid
2737 | 2 | 2100 | FM-08 | HY-11754 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 2100JNS96 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2738 | 2 | 2100 | FM-08 | ZSL-11754 | Valve Close | [5 empty] | FGDS | CRR | d | F | 2100JNS96 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2739 | 2 | 2100 | FM-08 | ZSH-11754 | Valve open | [5 empty] | FGDS | CRR | d | F | 2100JNS96 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2740 | 3 | 0000 | FM-08 | ZAH-11754B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2741 | 2 | 0003 | FM-08 | ZAH-11754C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2742 | 3 | 0000 | FM-08 | HS-11754B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2743 | 2 | 2100 | FM-08 | HS-11754A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2744 | 2 | 2100 | FM-08 | ZAH-11754 | Alarm valve Open
2745 | 2 | 2100 | FM-08 | ZAL-11754 | Alarm valve Close
2746 | 2 | 2100 | FM-08 | MR-11754 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2747 | 2 | 2100 | FM-09 | UV-11755 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Signal connection is seen through a use of Solenoid
2748 | 2 | 2100 | FM-09 | HY-11755 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 2100JNS97 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2749 | 2 | 2100 | FM-09 | ZSL-11755 | Valve Close | [5 empty] | FGDS | CRR | d | F | 2100JNS97 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2750 | 2 | 2100 | FM-09 | ZSH-11755 | Valve open | [5 empty] | FGDS | CRR | d | F | 2100JNS97 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2751 | 3 | 0000 | FM-09 | ZAH-11755B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2752 | 2 | 0003 | FM-09 | ZAH-11755C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2753 | 3 | 0000 | FM-09 | HS-11755B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2754 | 2 | 2100 | FM-09 | HS-11755A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2755 | 2 | 2100 | FM-09 | ZAH-11755 | Alarm valve Open
2756 | 2 | 2100 | FM-09 | ZAL-11755 | Alarm valve Close
2757 | 2 | 2100 | FM-09 | MR-11755 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2758 | 2 | 1000 | FM-10 | UV-10751 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Signal connection is seen through a use of Solenoid
2759 | 2 | 1000 | FM-10 | HY-10751 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 |  |  |  |  | d | F | 1000JNS80 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2760 | 2 | 1000 | FM-10 | ZSL-10751 | Valve Close | [5 empty] | FGDS | CRR | d | F | 1000JNS80 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2761 | 2 | 1000 | FM-10 | ZSH-10751 | Valve open | [5 empty] | FGDS | CRR | d | F | 1000JNS80 |  | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close
2762 | 3 | 0000 | FM-10 | ZAH-10751B | Valve open alarm at CCR |  | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2763 | 2 | 0003 | FM-10 | ZAH-10751C | Valve open alarm at GFAP |  | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2764 | 3 | 0000 | FM-10 | HS-10751B | Remote open from Matrix Panel | Hand switch Control room | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 |  |  | FGDS | CRR |  | MP | 1000CND25 |  | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2765 | 2 | 1000 | FM-10 | HS-10751A | Remote open from Software |  |  | ESBR-HS-CAF-0002
2766 | 2 | 1000 | FM-10 | ZAH-10751 | Alarm valve Open
2767 | 2 | 1000 | FM-10 | ZAL-10751 | Alarm valve Close
2768 | 2 | 1000 | FM-10 | MR-10751 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2769 | 2 | 2000 | FM-11 | UV-20752 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2770 | 4 | 2000 | FM-11 | HY-20752 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP05 | 1 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0001 |  |  |  | Signal connection is seen through a use of Solenoid
2771 | 4 | 2000 | FM-11 | ZSL-20752 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 2 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001 |  |  |  | Replaced by 2000JNS81
2772 | 4 | 2000 | FM-11 | ZSH-20752 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 3 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001
2773 | 3 | 0000 | FM-11 | ZAH-20752B | Valve open alarm at CCR | Valve open alarm at CCR FM-11 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2774 | 2 | 0003 | FM-11 | ZAH-20752C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-11 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2775 | 3 | 0000 | FM-11 | HS-20752B | Remote open from Matrix Panel | Hand switch Control room FM-11 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 4 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2776 | 4 | 0000 | FM-11 | XS-20752LB |  | Hand switch Lamp Control room FM-11 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2777 | 4 | 2000 | FM-11 | HS-20752 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP05 | 4 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2778 | 2 | 2000 | FM-11 | ZAH-20752 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2779 | 2 | 2000 | FM-11 | ZAL-20752 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2780 | 2 | 2000 | FM-11 | MR-20752 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2781 | 2 | 2000 | FM-12 | UV-20753 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2782 | 4 | 2000 | FM-12 | HY-20753 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP05 | 6 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0001 |  |  |  | Signal connection is seen through a use of Solenoid
2783 | 4 | 2000 | FM-12 | ZSL-20753 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 7 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001 |  |  |  | Replaced by 2000JNS82
2784 | 4 | 2000 | FM-12 | ZSH-20753 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 8 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001
2785 | 3 | 0000 | FM-12 | ZAH-20753B | Valve open alarm at CCR | Valve open alarm at CCR FM-12 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2786 | 2 | 0003 | FM-12 | ZAH-20753C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-12 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2787 | 3 | 0000 | FM-12 | HS-20753B | Remote open from Matrix Panel | Hand switch Control room FM-12 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 6 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2788 | 4 | 0000 | FM-12 | XS-20753LB |  | Hand switch Lamp Control room FM-12 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2789 | 4 | 2000 | FM-12 | HS-20753 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP05 | 9 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2790 | 2 | 2000 | FM-12 | ZAH-20753 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2791 | 2 | 2000 | FM-12 | ZAL-20753 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2792 | 2 | 2000 | FM-12 | MR-20753 | Manual Release |  | Hand Switch are usually connected in series with the solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  | d | F |  |  | 01-P-1.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | Open
2793 | 4 | 2000 | FM-17 | UV-20754 | Fire water Monitor Remote Control |  |  | ESBR-HS-PID-0016 | [25 empty] | Package, Signals are not finalised yet
2794 | 4 | 2000 | FM-17 | HY-20754 | Solenoid related to valve actuator |  |  | ESBR-HS-PID-1912 | DOR | NIS | FGDS | CRR | d | F | LCP05 | 11 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0001 |  |  |  | Signal connection is seen through a use of Solenoid
2795 | 4 | 2000 | FM-17 | ZSL-20754 | Valve Close |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 12 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001
2796 | 4 | 2000 | FM-17 | ZSH-20754 | Valve open |  |  | ESBR-HS-PID-0016 | DI | NIS | FGDS | CRR | d | F | LCP05 | 13 | 08-P-2.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | Close | [8 empty] | ESBR-CI-DWG-0001
2797 | 4 | 0000 | FM-17 | ZAH-20754B | Valve open alarm at CCR | Valve open alarm at CCR FM-17 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DOR | NIS | FGDS | CRR |  | MP | 1000CND27 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2798 | 4 | 0003 | FM-17 | ZAH-20754C | Valve open alarm at GFAP | Valve open alarm at GFAP FM-17 | Signal to GFAP In Fire station | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2799 | 4 | 0000 | FM-17 | HS-20754B | Remote open from Matrix Panel | Hand switch Control room FM-17 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DIR | NIS | FGDS | CRR |  | MP | 1000CND27 | 14 | 16-P-1.50-11-NAR-R-RD-N |  | ESBR-CI-DGR-0010/39_4 | SYS/24Vdc | Open
2800 | 4 | 0000 | FM-12 | XS-20754LB |  | Hand switch Lamp Control room FM-17 | Signal from Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0002 | DO | NIS | FGDS | CRR |  | MP |  |  | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Open
2801 | 4 | 2000 | FM-17 | HS-20754 | Remote open |  | Hand switch connected in series with solenoid | ESBR-HS-CAF-0002 |  | NIS |  |  |  | F | LCP05 | 14 | 08-P-2.50-11-SWA-S-RD-N | [16 empty] | Installed in safe area, connection in series with HY
2802 | 4 | 2000 | FM-17 | ZAH-20754 | Alarm valve Open |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2803 | 4 | 2000 | FM-17 | ZAL-20754 | Alarm valve Close |  |  | ESBR-HS-PID-1912 | [5 empty] | OWS
2804 | 3 | 7000 | SD-7000 | SA/HA-7000 | Status signal to FGS |  |  | ESBR-HS-CAF-0010 | DI | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2805 | 3 | 7000 | TGD-7000 | TGA-7000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0010 | DI | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-6
2806 | 3 | 7000 | MCP-7000 | MCP-7000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0010 | DI | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-6
2807 | 3 | 7000 | IRGD-7000 | IRGA-7000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0010 | DI | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2808 | 3 | 8000 | SD-8000 | SA/HA-8000 | Status signal to FGS |  |  | ESBR-HS-CAF-0009 | DI | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2809 | 3 | 8000 | TGD-8000 | TGA-8000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0009 | DI | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-7
2810 | 3 | 8000 | MCP-8000 | MCP-8000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0009 | DI | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002-7
2811 | 3 | 8000 | IRGD-8000 | IRGA-8000 | Status signal to FGS |  | Status signal From FAP TO FGS | ESBR-HS-CAF-0009 | DI | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [8 empty] | ESBR-CI-DWG-0002
2812 | 3 | 0000 | SD-7000 | SA/HA-7000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 7000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0010 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2813 | 3 | 0000 | TGD-7000 | TGA-7000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 7000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0010 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2814 | 3 | 0000 | MCP-7000 | MCP-7000B |  | MANUAL CALL POINT STATUS LAMP OF AREA 7000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0010 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2815 | 3 | 0000 | IRGD-7000 | IRGA-7000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 7000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0010 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2816 | 3 | 0000 | SD-8000 | SA/HA-8000B | Smoke, Signal to CCR | FIRE DETECTOR STATUS LAMP OF AREA 8000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0009 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2817 | 3 | 0000 | TGD-8000 | TGA-8000B | Toxic gas, Signal to CCR | TOXIC GAS DETECTOR STATUS LAMP OFAREA 8000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0009 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2818 | 3 | 0000 | MCP-8000 | MCP-8000B |  | MANUAL CALL POINT STATUS LAMP OF AREA8000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0009 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 14 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2819 | 3 | 0000 | IRGD-8000 | IRGA-8000B | Fire and Gas, Signal to CCR | FLAMMABLE GAS STATUS LAMP OF AREA 8000 | Signal to Matrix Panel Central Control Room (CCR) | ESBR-HS-CAF-0009 | DOR | NIS | FGDS | CRR |  | MP | 1000CND26 | 15 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | CLOSE
2820 | 3 | 0003 | SD-7000 | SA/HA-7000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 7000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2821 | 3 | 0003 | TGD-7000 | TGA-7000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 7000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2822 | 3 | 0003 | MCP-7000 | MCP-7000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA 7000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2823 | 3 | 0003 | IRGD-7000 | IRGA-7000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 7000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2824 | 3 | 0003 | SD-8000 | SA/HA-8000C | Signal connection through remote I/O | FIRE DETECTOR STATUS LAMP OF AREA 8000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2825 | 3 | 0003 | TGD-8000 | TGA-8000C | Signal connection through remote I/O | TOXIC GAS DETECTOR STATUS LAMP OF FIRE ZONE 8000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2826 | 3 | 0003 | MCP-8000 | MCP-8000C | Signal connection through remote I/O | MANUAL CALL POINT STATUS LAMP OF AREA8000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE
2827 | 3 | 0003 | IRGD-8000 | IRGA-8000C | Signal connection through remote I/O | FLAMMABLE GAS STATUS LAMP OF AREA 8000 | Signal to GFAP In Fire station | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | GFAP | N.A |  |  |  |  | SYS/24Vdc | CLOSE

## LFAP(Building)
SADAF ESBR PLANT (BANDAR ASSALOUYEH)
FGS I/O List
Owner Doc No.: ESBR-CI-LST-0005 | [13 empty] | Contractor Doc. No.: N-275-000-CI-LST-0000-005
Rev.: 4
Item No. | Rev | unit | Loop Number | TAG- Number | Service_1 | Service_2 | Description | PID/ F&G Detction Layout | I/O Type | Signal Type | Signal Conn. | Rack Room | Eex | Location | Junction Box |  | Cable Type | line no. | Typical Loop | Power Source | Input/Output Contact Activated State Action | Valve Failure Action | Low Range | High Range | Eng Units | High High Trip | High Alarm | Low Alarm | Low Low Trip | Control Action | Cable Routing No. | Data Sheet no. | Manufa cturer | Model no. | Remark
[15 empty] | JB No. | TB No.
2828 | 2 | 2000 | HDROR-2005 | HDROR-2018 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
2829 | 2 | 2000 | HDROR-2005 | HDROR-2017 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2830 | 2 | 2000 | HDROR-2005 | HDROR-2016 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2831 | 2 | 2000 | HDROR-2005 | HDROR-2015 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2832 | 2 | 2000 | HDROR-2005 | HDROR-2014 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2833 | 2 | 2000 | HDROR-2005 | HDROR-2013 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2834 | 2 | 2000 | HDROR-2005 | HDROR-2012 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2835 | 2 | 2000 | HDROR-2005 | HDROR-2011 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2836 | 2 | 2000 | HDROR-2005 | HDROR-2010 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2837 | 2 | 2000 | HDROR-2005 | HDROR-2009 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2838 | 2 | 2000 | HDROR-2005 | HDROR-2008 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2839 | 2 | 2000 | HDROR-2005 | HDROR-2007 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2840 | 2 | 2000 | HDROR-2005 | HDROR-2006 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2841 | 2 | 2000 | HDROR-2005 | HDROR-2005 | HeatDetector SuB station | Transformer Room | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS | LFAP |  | I | MCC | HDROR-2005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2842 | 4 | 2000 | HDROR-2001 | SD-2002 | Combined Heat/Smoke Detector Substation | BATTERY ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | SD-2002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2843 | 4 | 2000 | HDROR-2001 | HDROR-2004 | Combined Heat/Smoke Detector Substation | BATTERY ROOM | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2844 | 4 | 2000 | HDROR-2001 | HDROR-2003 | Combined Heat/Smoke Detector Substation | BATTERY ROOM | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2845 | 4 | 2000 | HDROR-2001 | SD-2001 | Combined Heat/Smoke Detector Substation | BATTERY ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | SD-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2846 | 4 | 2000 | HDROR-2001 | HDROR-2002 | Combined Heat/Smoke Detector Substation | DIESEL GENERATOR ROOM | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS |  |  | I | MCC | HDROR-2002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2847 | 4 | 2000 | HDROR-2001 | HDROR-2001 | Combined Heat/Smoke Detector Substation | DIESEL GENERATOR ROOM | Heat detectro Rate of Rise | ESBR-HS-LYT-0008 | AL | IS | LFAP |  | I | MCC | HDROR-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2848 | 2 | 2000 | SD2014 | SD-2003 | Combined Heat/Smoke Detector Substation | PDCS/RIO INTERFACE ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS | LFAP |  | SF | MCC | SD-2003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2849 | 2 | 2000 | SD2014 | SD-2004 | Combined Heat/Smoke Detector Substation | PDCS/RIO INTERFACE ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2850 | 2 | 2000 | SD2014 | SD-2016 | Combined Heat/Smoke Detector Substation | PDCS/RIO INTERFACE ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2851 | 2 | 2000 | SD2014 | SD-2018 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2852 | 2 | 2000 | SD2014 | SD-2005 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2853 | 2 | 2000 | SD2014 | SD-2006 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2854 | 2 | 2000 | SD2014 | SD-2019 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2855 | 2 | 2000 | SD2014 | SD-2020 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2856 | 2 | 2000 | SD2014 | SD-2007 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2019 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2857 | 2 | 2000 | SD2014 | SD-2021 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2020 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2858 | 2 | 2000 | SD2014 | SD-2017 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2021 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2859 | 2 | 2000 | SD2014 | SD-2009 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2860 | 2 | 2000 | SD2014 | SD-2008 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2861 | 2 | 2000 | SD2014 | SD-2011 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2862 | 2 | 2000 | SD2014 | SD-2010 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2863 | 2 | 2000 | SD2014 | SD-2023 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2023 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2864 | 2 | 2000 | SD2014 | SD-2022 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2022 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2865 | 2 | 2000 | SD2014 | SD-2024 | Combined Heat/Smoke Detector Substation | VFD ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2024 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2866 | 2 | 2000 | SD2014 | SD-2015 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2867 | 2 | 2000 | SD2014 | SD-2012 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2868 | 2 | 2000 | SD2014 | SD-2013 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2869 | 2 | 2000 | SD2014 | SD-2014 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | SD-2012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2870 | 2 | 2000 | SD2014 | SD-2025 | Combined Heat/Smoke Detector Substation | HVAC ROOM | Smoke detectorr | ESBR-HS-LYT-0008 | AL | NIS | LFAP |  | SF | MCC | SD-2025 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2871 | 3 | 2000 | HVAC-2000 | MHKL-Y2001 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0003 | DOR | NIS | LFAP |  |  | MCC | HVAC2000A | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2872 | 3 | 2000 | HVAC-2000 | MHKL-Y2002 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0003 | DOR | NIS | LFAP |  |  | MCC | HVAC2000A | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2873 | 3 | 2000 | HVAC-2000 | XL-Y2005 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0003 | DIR | NIS | LFAP |  |  | MCC | HVAC2000A | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2874 | 3 | 2000 | HVAC-2000 | XL-Y2006 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0003 | DIR | NIS | LFAP |  |  | MCC | HVAC2000A | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2875 | 3 | 2000 | HVAC-2000 | HVAC-Y2001 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0003 | DIR | NIS | LFAP |  |  | MCC | HVAC2000A | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2876 | 3 | 2000 | HVAC-2000 | HVAC-Y2002 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0003 | DIR | NIS | LFAP |  |  | MCC | HVAC2000A | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2877 | 3 | 2000 | HVAC-2000 | HVAC-2000A | Shutdown all HVAC System & Dampers Close of Sub station |  | Shutdown status signal of HVAC System & Close Dampers for Matrix Panel | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000A | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
2878 | 4 | 2000 | HVAC-2000 | XL-Y2008 | MFD-SUB-001 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2879 | 4 | 2000 | HVAC-2000 | XL-Y2009 | MFD-SUB-002 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2880 | 4 | 2000 | HVAC-2000 | XL-Y2010 | MFD-SUB-003 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2881 | 4 | 2000 | HVAC-2000 | XL-Y2011 | MFD-SUB-004 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2882 | 4 | 2000 | HVAC-2000 | XL-Y2012 | MFD-SUB-005 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2883 | 4 | 2000 | HVAC-2000 | XL-Y2013 | MFD-SUB-006 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2884 | 4 | 2000 | HVAC-2000 | XL-Y2014 | MFD-SUB-007 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000A | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2885 | 4 | 2000 | HVAC-2000 | XL-Y2015 | MFD-SUB-008 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2886 | 4 | 2000 | HVAC-2000 | XL-Y2016 | MFD-SUB-009 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2887 | 4 | 2000 | HVAC-2000 | XL-Y2017 | MFD-SUB-010 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2888 | 4 | 2000 | HVAC-2000 | XL-Y2018 | MFD-SUB-011 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2889 | 4 | 2000 | HVAC-2000 | XL-Y2019 | MFD-SUB-012 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2890 | 4 | 2000 | HVAC-2000 | XL-Y2020 | MFD-SUB-013 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2891 | 4 | 2000 | HVAC-2000 | XL-Y2021 | MFD-SUB-014 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2892 | 4 | 2000 | HVAC-2000 | XL-Y2022 | MFD-SUB-015 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2893 | 4 | 2000 | HVAC-2000 | XL-Y2023 | MFD-SUB-016 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2894 | 4 | 2000 | HVAC-2000 | XL-Y2024 | MFD-SUB-017 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2895 | 4 | 2000 | HVAC-2000 | XL-Y2025 | FGD-SUB-001 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2896 | 4 | 2000 | HVAC-2000 | XL-Y2026 | FGD-SUB-002 Status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐0003 | DI | NIS | LFAP |  |  | MCC | HVAC2000B | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
2897 | 2 | 2000 | MCP-2008 | MCP-2008 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS | LFAP |  | SF | MCC | MCP-2008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
2898 | 2 | 2000 | MCP-2008 | MCP-2009 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | MCP-2009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2899 | 2 | 2000 | MCP-2008 | MCP-2007 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | MCP-2007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2900 | 2 | 2000 | MCP-2008 | MCP-2003 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | MCP-2003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2901 | 2 | 2000 | MCP-2008 | MCP-2004 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | MCP-2004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2902 | 2 | 2000 | MCP-2008 | MCP-2005 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS |  |  | SF | MCC | MCP-2005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2903 | 2 | 2000 | MCP-2008 | MCP-2006 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | AL | NIS | LFAP |  | SF | MCC | MCP-2006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2904 | 4 | 2000 | MCP-2001 | MCP-2001 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | MCP-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2905 | 4 | 2000 | MCP-2002 | MCP-2002 | Manual Call point Inside Sub station | SS Indoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | MCP-2002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2906 | 3 | 2000 | MCP-2011 | MCP-2011 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND75 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2907 | 3 | 2000 | MCP-2010 | MCP-2010 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND74 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2908 | 3 | 2000 | MCP-2014 | MCP-2014 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2909 | 3 | 2000 | MCP-2016 | MCP-2016 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2910 | 3 | 2000 | MCP-2015 | MCP-2015 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2911 | 3 | 2000 | MCP-2012 | MCP-2012 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND72 | 4 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2912 | 3 | 2000 | MCP-2013 | MCP-2013 | Manual Call point Outside Sub station | SS Outdoor | Manual Call Point | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2913 | 1 | 2000 | MCP-2000 | MCP-2000 | Status signal to FGS |  |  | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2914 | 2 | 2000 | IRGD-2001 | IRGD/P-2001 | DIESEL GENERATOR ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2915 | 1 | 2000 | IRGD-2001 | IRGAH-2001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-LYT-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2916 | 1 | 2000 | IRGD-2001 | IRGAHH2001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2917 | 2 | 2000 | IRGD-2001 | XA-2001 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2918 | 1 | 2000 | IRGD-2000 | IRGA-2000 | Status signal to FGS |  |  | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2919 | 1 | 2000 | FD-2000 | FA-2000 |  |  |  | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000A | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2920 | 1 | 2000 | SD-2000 | SA-2000 | Status signal to FGS |  |  | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2921 | 3 | 2000 | EW-2001 | FSH-20751A | Status signal Flow switch |  |  | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000A | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2922 | 2 | 2000 | UK-2000 | UK-2000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Signals are included since there is no general alarm sound exists, these signals might be deleted.
2923 | 2 | 2000 | UK-2000 | UK-2000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2924 | 2 | 2000 | UK-2000 | UK-2000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2925 | 2 | 2000 | UL-2000 | UL-2000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2926 | 2 | 2000 | UL-2000 | UL-2000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2927 | 2 | 2000 | UL-2000 | UL-2000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
2928 | 2 | 2000 | EIS-2000 | EIS-2000 | Isolation of pewer supply | [5 empty] | LFAP | CRR |  | FGDS | EIS-2000 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
2929 | 2 | 2000 | EIS-2001 | EIS-2001 | Isolation of Battery feaders | [5 empty] | LFAP | CRR |  | FGDS | EIS-2001 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
2930 | 2 | 2000 | IRGD-2002 | IRGD/P-2002 | DIESEL GENERATOR ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2931 | 1 | 2000 | IRGD-2002 | IRGAH-2002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | EIS-3000 | [9 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2932 | 1 | 2000 | IRGD-2002 | IRGAHH2002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | EIS-3001 | [9 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2933 | 2 | 2000 | IRGD-2002 | XA-2002 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2934 | 2 | 2000 | IRGD-2003 | IRGD/P-2003 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2935 | 1 | 2000 | IRGD-2003 | IRGAH-2003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2936 | 1 | 2000 | IRGD-2003 | IRGAHH2003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2937 | 2 | 2000 | IRGD-2003 | XA-2003 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2938 | 2 | 2000 | IRGD-2004 | IRGD/P-2004 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2939 | 1 | 2000 | IRGD-2004 | IRGAH-2004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2940 | 1 | 2000 | IRGD-2004 | IRGAHH2004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2941 | 2 | 2000 | IRGD-2004 | XA-2004 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2942 | 2 | 2000 | IRGD-2005 | IRGD/P-2005 | TRANSFORMER | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2943 | 1 | 2000 | IRGD-2005 | IRGAH-2005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2944 | 1 | 2000 | IRGD-2005 | IRGAHH2005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2945 | 2 | 2000 | IRGD-2005 | XA-2005 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2946 | 2 | 2000 | IRGD-2006 | IRGD/P-2006 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2947 | 2 | 2000 | IRGD-2006 | IRGAH-2006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2948 | 2 | 2000 | IRGD-2006 | IRGAHH2006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2949 | 2 | 2000 | IRGD-2006 | XA-2015 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2950 | 2 | 2000 | IRGD-2007 | IRGD/P-2007 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | IRGD-2006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2951 | 2 | 2000 | IRGD-2007 | IRGAH-2007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
2952 | 2 | 2000 | IRGD-2007 | IRGAHH2007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
2953 | 2 | 2000 | IRGD-2007 | XA-2016 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2954 | 2 | 2000 | TGD-2001 | TGD-2001 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | TGD-2001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2955 | 1 | 2000 | TGD-2001 | TGAH-2001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) |  | 50 |  |  |  |  | ESBR-CI-DAS-0030
2956 | 1 | 2000 | TGD-2001 | TGAHH-2001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) | 100 | [5 empty] | ESBR-CI-DAS-0030
2957 | 2 | 2000 | TGD-2001 | XA-2006 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XL-2006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2958 | 2 | 2000 | TGD-2002 | TGD-2002 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | TGD-2002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2959 | 1 | 2000 | TGD-2002 | TGAH-2002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) |  | 50 |  |  |  |  | ESBR-CI-DAS-0030
2960 | 1 | 2000 | TGD-2002 | TGAHH-2002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) | 100 | [5 empty] | ESBR-CI-DAS-0030
2961 | 2 | 2000 | TGD-2002 | XA-2007 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XL-2007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2962 | 2 | 2000 | TGD-2003 | TGD-2003 | TRANSFORMER |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | TGD-2003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2963 | 1 | 2000 | TGD-2003 | TGAH-2003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) |  | 50 |  |  |  |  | ESBR-CI-DAS-0030
2964 | 1 | 2000 | TGD-2003 | TGAHH-2003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) | 100 | [5 empty] | ESBR-CI-DAS-0030
2965 | 2 | 2000 | TGD-2003 | XA-2008 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2966 | 2 | 2000 | TGD-2004 | TGD-2004 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | TGD-2004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2967 | 2 | 2000 | TGD-2004 | TGAH-2004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) |  | 50 |  |  |  |  | ESBR-CI-DAS-0030
2968 | 2 | 2000 | TGD-2004 | TGAHH-2004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) | 100 | [5 empty] | ESBR-CI-DAS-0030
2969 | 2 | 2000 | TGD-2004 | XA-2013 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2970 | 2 | 2000 | TGD-2005 | TGD-2005 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0008 | AIR | NIS | LFAP |  | d | MCC | TGD-2005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2971 | 2 | 2000 | TGD-2005 | TGAH-2005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) |  | 50 |  |  |  |  | ESBR-CI-DAS-0030
2972 | 2 | 2000 | TGD-2005 | TGAHH-2005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | (TLV-TWA) | 100 | [5 empty] | ESBR-CI-DAS-0030
2973 | 2 | 2000 | TGD-2005 | XA-2014 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2974 | 1 | 2000 | TGD-2000 | TGA-2000 | Status signal to FGS |  |  | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2975 | 1 | 2000 | HGD-2000 | HGA-2000 | Status signal to FGS |  |  | ESBR-HS-CAF-0003 | DO | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2976 | 4 | 2000 | LFAP-2000 | LFXA-2000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2977 | 4 | 2000 | LFAP-2000 | LFXF-2000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-2000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2978 | 4 | 2000 | HGD-2001 | HGD-2001 | BATTERY ROOM | Point Type Gas Detector | Flammable. Gas (Hydrogen) | ESBR-HS-LYT-0008 | AIR | IS | LFAP |  | I | MCC | H2D-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2979 | 1 | 2000 | HGD-2001 | HGAH-2001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH LEVEL 5%OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 5 |  |  |  |  | ESBR-CI-DAS-0030
2980 | 1 | 2000 | HGD-2001 | HGAHH2001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH HIGH LEVEL 10% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 10 | [5 empty] | ESBR-CI-DAS-0030
2981 | 4 | 2000 | HGD-2001 | XA-2009 |  |  | Fault | ESBR-HS-CAF-0003 | DI | IS | LFAP |  | I | MCC | XA-2009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2982 | 4 | 2000 | HGD-2002 | HGD-2002 | BATTERY ROOM | Point Type Gas Detector | Flammable. Gas (Hydrogen) | ESBR-HS-LYT-0008 | AIR | IS | LFAP |  | I | MCC | H2D-2002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
2983 | 1 | 2000 | HGD-2002 | HGAH-2002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH LEVEL 5%OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL |  | 5 |  |  |  |  | ESBR-CI-DAS-0030
2984 | 1 | 2000 | HGD-2002 | HGAHHP2002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH HIGH LEVEL 10% OF LFL | ESBR-HS-CAF-0003 | [5 empty] | MCC | [10 empty] | %LFL | 10 | [5 empty] | ESBR-CI-DAS-0030
2985 | 4 | 2000 | HGD-2002 | XA-2010 |  |  | Fault | ESBR-HS-CAF-0003 | DI | IS | LFAP |  | I | MCC | XA-2010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2986 | 2 | 2000 | UK-2001 | UK-2001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2987 | 2 | 2000 | UK-2001 | UK-2001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2988 | 2 | 2000 | UK-2001 | UK-2001A |  |  |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2989 | 4 | 2000 | UL-2001 | UL-2001A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2990 | 4 | 2000 | UL-2001 | UL-2001C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2991 | 4 | 2000 | UL-2001 | UL-2001B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2992 | 2 | 2000 | UK-2002 | UK-2002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2993 | 2 | 2000 | UK-2002 | UK-2002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2994 | 2 | 2000 | UK-2002 | UK-2002A |  |  |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2995 | 4 | 2000 | UL-2002 | UL-2002A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2996 | 4 | 2000 | UL-2002 | UL-2002C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2997 | 4 | 2000 | UL-2002 | UL-2002B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND75 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2998 | 2 | 2000 | UK-2003 | UK-2003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
2999 | 2 | 2000 | UK-2003 | UK-2003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3000 | 2 | 2000 | UK-2003 | UK-2003A |  |  |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3001 | 4 | 2000 | UL-2003 | UL-2003A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3002 | 4 | 2000 | UL-2003 | UL-2003C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On Hold
3003 | 4 | 2000 | UL-2003 | UL-2003B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3004 | 2 | 2000 | UK-2004 | UK-2004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3005 | 2 | 2000 | UK-2004 | UK-2004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3006 | 2 | 2000 | UK-2004 | UK-2004A |  |  |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3007 | 4 | 2000 | UL-2004 | UL-2004A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3008 | 4 | 2000 | UL-2004 | UL-2004C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On hold
3009 | 4 | 2000 | UL-2004 | UL-2004B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3010 | 2 | 2000 | UK-2006 | UK-2006B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3011 | 2 | 2000 | UK-2006 | UK-2006C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3012 | 2 | 2000 | UK-2006 | UK-2006A |  |  |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3013 | 4 | 2000 | UL-2006 | UL-2006A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On Hold
3014 | 4 | 2000 | UL-2006 | UL-2006C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On Hold
3015 | 4 | 2000 | UL-2006 | UL-2006B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3016 | 2 | 2000 | UK-2005 | UK-2005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3017 | 2 | 2000 | UK-2005 | UK-2005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3018 | 2 | 2000 | UK-2005 | UK-2005A |  | MCP/Fire |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3019 | 4 | 2000 | UL-2005 | UL-2005A | (YELLOW FLASHING LIGHT) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On Hold
3020 | 4 | 2000 | UL-2005 | UL-2005C | (GREEN FLASHING LIGHT) | (25% LFL) or (50% LFL) IRGD | FLASHING LIGHT | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | On Hold
3021 | 4 | 2000 | UL-2005 | UL-2005B |  | MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MCC | 2000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3022 | 2 | 2000 | UK-2007 | UK-2007B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2007 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3023 | 2 | 2000 | UK-2007 | UK-2007C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2007 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3024 | 2 | 2000 | UK-2007 | UK-2007A |  | MCP/Fire |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2007 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3025 | 2 | 2000 | UK-2008 | UK-2008B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2008 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3026 | 2 | 2000 | UK-2008 | UK-2008C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2008 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3027 | 2 | 2000 | UK-2008 | UK-2008A |  | MCP/Fire |  | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | SF | MCC | UK-2008 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3028 | 3 | 2000 | EWSD-2001 | EWSA-2001 | Activation Clean agent Main | On Hold | Early warning smoke detector | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND77 | 1 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3029 | 3 | 2000 | EWSD-2001 | EWXA-2001 | Activation of clean agent False Floor | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND77 | 2 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3030 | 3 | 2000 | EWSD-2001 | EWSA-2001 | System Fault | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND77 | 3 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3031 | 1 | 2000 | EWSD-2000 | EWSA-2000 | Alarm from FAP to FGS | On Hold |  | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3032 | 2 | 2000 | EWSD-2000 | EWXF-2000 | FAULT |  |  | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000A | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3033 | 3 | 2000 | EWSD-2002 | EWSA-2002 | Activation Clean agent Main | On Hold | Early warning smoke detector | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND78 | 1 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3034 | 3 | 2000 | EWSD-2002 | EWXA-2002 | Activation of clean agent False Floor | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND78 | 2 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3035 | 3 | 2000 | EWSD-2002 | EWSA-2002 | System Fault | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | MCC | 2000JND78 | 3 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3036 | 2 | 2000 | FD-2001 | FD-2001 | DIESEL GENERATOR ROOM |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-0008 | AI | NIS | LFAP |  | d | MCC | FD-2001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3037 | 1 | 2000 | FD-2001 | FAH-2001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0003 | [6 empty] | FD-2002
3038 | 1 | 2000 | FD-2001 | XA-2011 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | FD-4001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
FD-4002
3039 | 2 | 2000 | FD-2002 | FD-2002 | DIESEL GENERATOR ROOM |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-0008 | AI | NIS | LFAP |  | d | MCC | FD-2002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3040 | 1 | 2000 | FD-2002 | FAH-2002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0003
3041 | 1 | 2000 | FD-2002 | XA-2012 |  |  | Fault | ESBR-HS-CAF-0003 | DI | NIS | LFAP |  | d | MCC | XA-2012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3042 | 2 | 2000 | CLA-2000 | YS-Y2000 | Clean Agent |  | Lockoff switch closed | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | Package inter cable connection , signals are not finalised.
3043 | 2 | 2000 | CLA-2000 | YS-Y2002 |  |  | Lockoff switch closed | ESBR-HS-PID-0002 |  |  | LFAP |  |  | MCC | CLAP-2000A | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3044 | 2 | 2000 | CLA-2000 | XS-Y2001 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT SWITCHGEAR ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3045 | 2 | 2000 | CLA-2000 | XS-Y2002 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT CABLE ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3046 | 2 | 2000 | CLA-2000 | XS-Y2003 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT PDCS/RIO ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3047 | 2 | 2000 | CLA-2000 | XS-Y2004 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT VFD ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3048 | 2 | 2000 | CLA-2000 | XL-Y2001 |  |  | DEACTIVATION OF CLEAN AGENT AT SWITCHGEAR ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3049 | 2 | 2000 | CLA-2000 | XL-Y2002 |  |  | DEACTIVATION OF CLEAN AGENT AT CABLE ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3050 | 2 | 2000 | CLA-2000 | XL-Y2003 |  |  | DEACTIVATION OF CLEAN AGENT AT PDCS/RIO ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3051 | 2 | 2000 | CLA-2000 | XL-Y2004 |  |  | DEACTIVATION OF CLEAN AGENT AT VFD ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3052 | 2 | 2000 | CLA-2000 | CSS-Y2011 |  |  | Clean Agent (auto Mode) SWITCHGEAR ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3053 | 2 | 2000 | CLA-2000 | CSS-Y2012 |  |  | Clean agent (Manule Mode)SWITCHGEAR ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3054 | 2 | 2000 | CLA-2000 | CSS-Y2013 |  |  | Clean agent (Inhibite Mode)SWITCHGEAR ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000A | 13 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3055 | 2 | 2000 | CLA-2000 | CSS-Y2021 |  |  | Clean Agent (auto Mode) CABLE ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3056 | 2 | 2000 | CLA-2000 | CSS-Y2022 |  |  | Clean agent (Manule Mode)CABLE ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3057 | 2 | 2000 | CLA-2000 | CSS-Y2023 |  |  | Clean agent (Inhibite Mode)CABLE ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3058 | 2 | 2000 | CLA-2000 | CSS-Y2031 |  |  | Clean Agent (auto Mode) PDCS/RIO ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3059 | 2 | 2000 | CLA-2000 | CSS-Y2032 |  |  | Clean agent (Manule Mode)PDCS/RIO ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3060 | 2 | 2000 | CLA-2000 | CSS-Y2033 |  |  | Clean agent (Inhibite Mode)PDCS/RIO ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3061 | 2 | 2000 | CLA-2000 | CSS-Y2041 |  |  | Clean Agent (auto Mode) VFD ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3062 | 2 | 2000 | CLA-2000 | CSS-Y2042 |  |  | Clean agent (Manule Mode)VFD ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3063 | 2 | 2000 | CLA-2000 | CSS-Y2043 |  |  | Clean agent (Inhibite Mode)VFD ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3064 | 2 | 2000 | CLA-2000 | PAH-Y2000 |  |  | Clean agent activated | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3065 | 2 | 2000 | CLA-2000 | XS-Y2000 |  |  | Clean agent auto discharge Command | ESBR-HS-PID-0002 | DOR | NIS | LFAP |  |  | MCC | CLAP-2000B | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3066 | 2 | 2000 | CLA-2000 | CLXA-Y2000 |  |  | fault signal | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3067 | 2 | 2000 | CLA-2000 | WAL-2000 |  |  | Weight loss capsules | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | MCC | CLAP-2000B | 13 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3068 | 2 | 2000 | CLA-2000 | SOV-2001 |  |  | Actuation of clean agent | ESBR-HS-PID-0002 |  |  | LFAP |  |  | MCC | CLAP-2000A |  | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3069 | 2 | 2000 | CLA-2000 | SOV-2002 |  |  | Actuation of clean agent | ESBR-HS-PID-0002 |  |  | LFAP |  |  | MCC | CLAP-2000A |  | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | Signals will be modified based on vendoe data
3070 | 4 | 2000 | CLA-2000 | CLXA-Y2003A | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3071 | 2 | 2000 | CLA-2000 | CSA-Y2000A | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3072 | 4 | 2000 | CLA-2000 | CLXA-Y2001A | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3073 | 4 | 2000 | CLA-2000 | CLXA-Y2002A | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3074 | 4 | 2000 | CLA-2000 | CLXA-Y2000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3075 | 2 | 2000 | CLA-2000 | YSA-Y2000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3076 | 2 | 2000 | CLA-2000 | WAL-Y2000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0003 | DO | NIS | LFAP | CRR |  | FGDS | CAP-2000B | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3077 | 3 | 2000 | EW-2001 | FSH-20751 | Safety Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | LFAP |  | SF | F | EW-2001 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3078 | 3 | 2000 | EW-2001 | FAH-20751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
3079 | 3 | 2000 | EW-2001 | FO-20751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
3080 | 4 | 1000 | HVAC-1000 | MHKL-Y1001 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0004 | DOR | NIS | LFAP |  |  | CCR | HVAC1000 A | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3081 | 4 | 1000 | HVAC-1000 | MHKL-Y1002 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0004 | DOR | NIS | LFAP |  |  | CCR | HVAC1000A | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3082 | 4 | 1000 | HVAC-1000 | XL-Y1005 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0004 | DIR | NIS | LFAP |  |  | CCR | HVAC1000A | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3083 | 4 | 1000 | HVAC-1000 | XL-Y1006 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0004 | DIR | NIS | LFAP |  |  | CCR | HVAC1000A | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3084 | 4 | 1000 | HVAC-1000 | HVAC-Y1001 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0004 | DIR | NIS | LFAP |  |  | CCR | HVAC1000A | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3085 | 4 | 1000 | HVAC-1000 | HVAC-Y1002 | HVAC shutdown status from Panel |  | HVAC signals to FGS | ESBR-HS-CAF-0004 | DIR | NIS | LFAP |  |  | CCR | HVAC1000A | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3086 | 4 | 1000 | HVAC-1000 | HVAC-1000A | Shutdown all HVAC System & Dampers Close of Sub station |  | Shutdown status signal of HVAC System & Close Dampers for Matrix Panel | ESBR-HS-CAF-0004 | DOR | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 |  |  |  | ON HOLD, Signals will be modified based on vendor data
3087 | 4 | 1000 | HVAC-1000 | XL-Y1005 | THE FRESH AIR INTAKE SHALL BE KEPT OPEN TO DECREASE THE HYDROGEN CONCENTRATION IN THE BATTERY ROOM |  | HVAC Status to LFAP | ESBR-HS-CAF-0004 | DIR | NIS | LFAP |  |  | CCR | HVAC1000A | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3088 | 4 | 1000 | HVAC-1000 | XL-Y1006 | MFD-CLB-001 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3089 | 4 | 1000 | HVAC-1000 | XL-Y1007 | MFD-CLB-002 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3090 | 4 | 1000 | HVAC-1000 | XL-Y1008 | MFD-CLB-003 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3091 | 4 | 1000 | HVAC-1000 | XL-Y1009 | MFD-CLB-004 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3092 | 4 | 1000 | HVAC-1000 | XL-Y1010 | MFD-CLB-005 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3093 | 4 | 1000 | HVAC-1000 | XL-Y1011 | MFD-CLB-006 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000A | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3094 | 4 | 1000 | HVAC-1000 | XL-Y1012 | MFD-CLB-007 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3095 | 4 | 1000 | HVAC-1000 | XL-Y1013 | MFD-CLB-008 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3096 | 4 | 1000 | HVAC-1000 | XL-Y1014 | MFD-CLB-009 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3097 | 4 | 1000 | HVAC-1000 | XL-Y1015 | MFD-CLB-010 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3098 | 4 | 1000 | HVAC-1000 | XL-Y1016 | MFD-CLB-011 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3099 | 4 | 1000 | HVAC-1000 | XL-Y1017 | MFD-CLB-012 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3100 | 4 | 1000 | HVAC-1000 | XL-Y1018 | MFD-CLB-013 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3101 | 4 | 1000 | HVAC-1000 | XL-Y1019 | MFD-CLB-014 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3102 | 4 | 1000 | HVAC-1000 | XL-Y1020 | MFD-CLB-015 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3103 | 4 | 1000 | HVAC-1000 | XL-Y1021 | MFD-CLB-016 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3104 | 4 | 1000 | HVAC-1000 | XL-Y1022 | MFD-CLB-017 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3105 | 4 | 1000 | HVAC-1000 | XL-Y1023 | FGD‐CLB‐001 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3106 | 4 | 1000 | HVAC-1000 | XL-Y1024 | FGD‐CLB‐002 Status |  | HVAC Status to LFAP | ESBR‐HV‐PID‐0004 | DI | NIS | LFAP |  |  | CCR | HVAC1000B | 13 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3107 | 1 | 1000 | IRGD-1000 | IRGA-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3108 | 1 | 1000 | FD-1000 | FA-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 |  |  | LFAP | CRR |  | FGDS | CAP-1000A |  | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3109 | 1 | 1000 | SD-1000 | SA-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3110 | 1 | 1000 | TGD-1000 | TGA-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3111 | 1 | 1000 | MCP-1000 | MCP-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3112 | 2 | 1000 | HGD-1000 | HGA-1000 | Status signal to FGS |  |  | ESBR-HS-CAF-0004 | DO | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3113 | 4 | 1000 | LFAP-1000 | LFXA-1000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3114 | 4 | 1000 | LFAP-1000 | LFXF-1000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-1000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3115 | 2 | 1000 | UK-1000 | UK-1000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3116 | 2 | 1000 | UK-1000 | UK-1000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3117 | 2 | 1000 | UK-1000 | UK-1000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3118 | 4 | 1000 | UL-1000 | UL-1000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3119 | 4 | 1000 | UL-1000 | UL-1000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3120 | 4 | 1000 | UL-1000 | UL-1000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3121 | 2 | 1000 | EIS-1000 | EIS-1000 | Isolation of pewer supply | [5 empty] | LFAP | CRR |  | FGDS | EIS-1000 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3122 | 2 | 1000 | EIS-1001 | EIS-1001 | Isolation of Battery feaders | [5 empty] | LFAP | CRR |  | FGDS | EIS-1001 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3123 | 2 | 1000 | SD-1007 | SD-1007 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | SD-1007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3124 | 2 | 1000 | SD-1007 | SD-1008 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3125 | 2 | 1000 | SD-1007 | SD-1040 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1036 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3126 | 2 | 1000 | SD-1007 | SD-1036 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1037 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3127 | 2 | 1000 | SD-1007 | SD-1038 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1038 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3128 | 2 | 1000 | SD-1007 | SD-1042 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1039 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3129 | 2 | 1000 | SD-1007 | SD-1013 | Engineering Room | Engineering Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3130 | 2 | 1000 | SD-1007 | SD-1046 | Engineering Room | Engineering Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3131 | 2 | 1000 | SD-1007 | SD-1017 | PLANT MANAGER ROOM | PLANT MANAGER ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3132 | 2 | 1000 | SD-1007 | SD-1019 | ARCHIVE ROOM | PLANT MANAGER ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3133 | 2 | 1000 | SD-1007 | SD-1020 | LABORATORY MANAGER ROOM | ARCHIVE ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1019 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3134 | 2 | 1000 | SD-1007 | SD-1021 | Confrance Room | LABORATORY MANAGER ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | d* | CCR | SD-1020 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3135 | 2 | 1000 | SD-1007 | SD-1022 | Staff Room | Confrance Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1021 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3136 | 2 | 1000 | SD-1007 | SD-1023 | Documantry Room | Staff Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1022 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3137 | 2 | 1000 | SD-1007 | SD-1024 | Corridor | Documantry Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1023 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3138 | 2 | 1000 | SD-1007 | SD-1025 | Corridor | Corridor | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1024 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3139 | 2 | 1000 | SD-1007 | SD- 1018 | PLANT MANAGER ROOM | Corridor | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1025 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3140 | 2 | 1000 | SD-1007 | SD-1047 | Engineering Room | Engineering Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1047 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3141 | 2 | 1000 | SD-1007 | SD-1014 | Engineering Room | Engineering Room | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1046 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3142 | 2 | 1000 | SD-1007 | SD-1039 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1043 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3143 | 2 | 1000 | SD-1007 | SD-1043 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1042 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3144 | 2 | 1000 | SD-1007 | SD-1041 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1041 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3145 | 2 | 1000 | SD-1007 | SD-1037 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1040 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3146 | 2 | 1000 | SD-1007 | SD-1009 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3147 | 2 | 1000 | SD-1007 | SD-1010 | CONTROL ROOM | CONTROL ROOM | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | SD-1008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3148 | 4 | 1000 | HDROR-1001 | SD-1029 | GC ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1029 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3149 | 4 | 1000 | HDROR-1001 | SD-1028 | SAMPLE STORAGE ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1028 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3150 | 4 | 1000 | HDROR-1001 | SD-1027 | CHEMICAL TEST LAB. | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1027 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3151 | 4 | 1000 | HDROR-1001 | HDROR-1003 | CHEMICAL TEST LAB. | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | HDROR-1003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3152 | 4 | 1000 | HDROR-1001 | SD-1049 | CHEMICAL TEST LAB. | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1049 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3153 | 4 | 1000 | HDROR-1001 | SD-1026 | PHYSICAL TEST LAB. | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1026 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3154 | 4 | 1000 | HDROR-1001 | SD-1016 | Chemical storage | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3155 | 4 | 1000 | HDROR-1001 | SD-1050 | BATTERY ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1050 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3156 | 4 | 1000 | HDROR-1001 | HDROR-1004 | BATTERY ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | HDROR-1004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3157 | 4 | 1000 | HDROR-1001 | SD-1002 | BATTERY ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | SD-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3158 | 4 | 1000 | HDROR-1001 | MCP-1003 | BATTERY ROOM | IS Loop | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | IS |  |  | I | CCR | HDROR-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3159 | 4 | 1000 | HDROR-1001 | HDROR-1001 | BATTERY ROOM | IS Loop | Manual Call point | ESBR-HS-LYT-0009 | AL | IS | LFAP |  | I | CCR | MCP-1003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3160 | 2 | 1000 | SD-1001 | SD-1001 | CLEAN AGENT ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | SD-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3161 | 2 | 1000 | SD-1001 | SD-1003 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3162 | 2 | 1000 | SD-1001 | SD-1004 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3163 | 2 | 1000 | SD-1001 | SD-1044 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3164 | 2 | 1000 | SD-1001 | SD-1005 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3165 | 2 | 1000 | SD-1001 | SD-1006 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1044 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3166 | 2 | 1000 | SD-1001 | SD-1045 | UPS ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1045 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3167 | 2 | 1000 | SD-1001 | SD-1011 | SHIFT SUPERVISOR ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3168 | 2 | 1000 | SD-1001 | SD-1012 | SHIFT SUPERVISOR ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3169 | 2 | 1000 | SD-1001 | SD-101 5 | CORRIDOR |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3170 | 2 | 1000 | SD-1001 | SD-1048 | CORRIDOR |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1048 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3171 | 2 | 1000 | SD-1001 | HDOROR -1002 | KITCHEN |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | HDROR-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3172 | 2 | 1000 | SD-1001 | SD-1034 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1034 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3173 | 2 | 1000 | SD-1001 | SD-1035 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1035 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3174 | 2 | 1000 | SD-1001 | SD-1033 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1033 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3175 | 2 | 1000 | SD-1001 | SD-1032 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1032 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3176 | 2 | 1000 | SD-1001 | SD-1031 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | SD-1031 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3177 | 2 | 1000 | SD-1001 | SD-1030 | HVAC ROOM |  | Combined Heat/Smoke Detector Control Room | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | SD-1030 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3178 | 2 | 1000 | MCP-1001 | MCP-1001 | CCR Indoor | CONTROL ROOM | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | MCP-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3179 | 2 | 1000 | MCP-1001 | MCP-1002 | CCR Indoor | CLEAN AGENT ROOM | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3180 | 2 | 1000 | MCP-1001 | MCP-1004 | CCR Indoor | UPS ROOM | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3181 | 2 | 1000 | MCP-1001 | MCP-1005 | CCR Indoor | AIR LOCK | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3182 | 2 | 1000 | MCP-1001 | MCP-1006 | CCR Indoor | CORRIDOR | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3183 | 2 | 1000 | MCP-1001 | MCP-1007 | CCR Indoor | HVAC ROOM | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3184 | 2 | 1000 | MCP-1001 | MCP-1009 | CCR Indoor | CORRIDOR | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS |  |  | SF | CCR | MCP-1009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3185 | 2 | 1000 | MCP-1001 | MCP-1008 | CCR Indoor | CORRIDOR | Manual Call point | ESBR-HS-LYT-0009 | AL | NIS | LFAP |  | SF | CCR | MCP-1008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3186 | 3 | 1000 | MCP-1013 | MCP-1013 | Outside Area |  | Manual Call point | ESBR-HS-LYT-0009 | DIR | NIS | LFAP |  | d* | CCR | 1000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3187 | 3 | 1000 | MCP-1012 | MCP-1012 | Outside Area |  | Manual Call point | ESBR-HS-LYT-0009 | DIR | NIS | LFAP |  | d* | CCR | 1000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3188 | 3 | 1000 | MCP-1011 | MCP-1011 | Outside Area |  | Manual Call point | ESBR-HS-LYT-0009 | DIR | NIS | LFAP |  | d* | CCR | 1000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3189 | 3 | 1000 | MCP-1010 | MCP-1010 | Outside Area |  | Manual Call point | ESBR-HS-LYT-0009 | DIR | NIS | LFAP |  | d* | CCR | 1000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3190 | 2 | 1000 | IRGD-1001 | IRGD/P-1001 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD-1001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3191 | 1 | 1000 | IRGD-1001 | IRGAH-1001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3192 | 1 | 1000 | IRGD-1001 | IRGAHH1001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3193 | 2 | 1000 | IRGD-1001 | XA-1001 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3194 | 2 | 1000 | IRGD-1002 | IRGD/P-1002 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD-1002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3195 | 1 | 1000 | IRGD-1002 | IRGAH-1002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3196 | 1 | 1000 | IRGD-1002 | IRGAHH1002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3197 | 2 | 1000 | IRGD-1002 | XA-1002 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3198 | 2 | 1000 | IRGD-1003 | IRGD/P-1003 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD-1003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3199 | 1 | 1000 | IRGD-1003 | IRGAH-1003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3200 | 1 | 1000 | IRGD-1003 | IRGAHH1003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3201 | 2 | 1000 | IRGD-1003 | XA-1003 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3202 | 2 | 1000 | IRGD-1004 | IRGD/P-1004 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD-1004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3203 | 1 | 1000 | IRGD-1004 | IRGAH-1004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3204 | 1 | 1000 | IRGD-1004 | IRGAHH1004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3205 | 2 | 1000 | IRGD-1004 | XA-1004 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3206 | 2 | 1000 | IRGD-1005 | IRGD/P-1005 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD-1005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3207 | 2 | 1000 | IRGD-1005 | IRGAH-1005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3208 | 2 | 1000 | IRGD-1005 | IRGAHH1005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3209 | 2 | 1000 | IRGD-1005 | XA-1010 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3210 | 2 | 1000 | IRGD-1006 | IRGD/P-1006 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | IRGD/P-1006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3211 | 2 | 1000 | IRGD-1006 | IRGAH-1006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 10
3212 | 2 | 1000 | IRGD-1006 | IRGAHH1006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 25
3213 | 2 | 1000 | IRGD-1006 | XA-1011 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3214 | 2 | 1000 | TGD-1001 | TGD-1001 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3215 | 1 | 1000 | TGD-1001 | TGAH-1001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3216 | 1 | 1000 | TGD-1001 | TGAHH-1001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3217 | 2 | 1000 | TGD-1001 | XA-1005 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3218 | 2 | 1000 | TGD-1002 | TGD-1002 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3219 | 1 | 1000 | TGD-1002 | TGAH-1002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3220 | 1 | 1000 | TGD-1002 | TGAHH-1002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3221 | 2 | 1000 | TGD-1002 | XA-1006 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3222 | 2 | 1000 | TGD-1003 | TGD-1003 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3223 | 1 | 1000 | TGD-1003 | TGAH-1003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3224 | 1 | 1000 | TGD-1003 | TGAHH-1003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3225 | 2 | 1000 | TGD-1003 | XA-1007 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3226 | 2 | 1000 | TGD-1004 | TGD-1004 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3227 | 1 | 1000 | TGD-1004 | TGAH-1004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3228 | 1 | 1000 | TGD-1004 | TGAHH-1004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3229 | 2 | 1000 | TGD-1004 | XA-1008 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3230 | 2 | 1000 | TGD-1005 | TGD-1005 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3231 | 2 | 1000 | TGD-1005 | TGAH-1005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3232 | 2 | 1000 | TGD-1005 | TGAHH-1005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3233 | 2 | 1000 | TGD-1005 | XA-1012 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3234 | 2 | 1000 | TGD-1006 | TGD-1006 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0009 | AIR | NIS | LFAP |  | d | CCR | TGD-1006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3235 | 2 | 1000 | TGD-1006 | TGAH-1006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3236 | 2 | 1000 | TGD-1006 | TGAHH-1006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3237 | 2 | 1000 | TGD-1006 | XA-1013 |  |  | Fault | ESBR-HS-CAF-0004 | DI | NIS | LFAP |  | d | CCR | XA-1013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3238 | 4 | 1000 | HGD-1001 | HGD-1001 | BATTERY ROOM | Point Type Gas Detector | Flammable. Gas (Hydrogen) | ESBR-HS-LYT-0009 | AIR | IS | LFAP |  | I | CCR | HGD-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3239 | 1 | 1000 | HGD-1001 | HGAH-1001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH LEVEL 5%OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 5
3240 | 1 | 1000 | HGD-1001 | HGAHH1001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH HIGH LEVEL 10% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 10
3241 | 4 | 1000 | HGD-1001 | XA-1009 |  |  | Fault | ESBR-HS-CAF-0004 | DI | IS | LFAP |  | I | CCR | XL-1009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3242 | 4 | 1000 | HGD-1002 | HGD-1002 | BATTERY ROOM | Point Type Gas Detector | Flammable. Gas (Hydrogen) | ESBR-HS-LYT-0009 | AIR | IS | LFAP |  | I | CCR | HGD-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3243 | 2 | 1000 | HGD-1002 | HGAH-1002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH LEVEL 5%OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL |  | 5
3244 | 2 | 1000 | HGD-1002 | HGAHH1002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | HGD HIGH HIGH LEVEL 10% OF LFL | ESBR-HS-CAF-0004 | [5 empty] | CCR | [10 empty] | %LFL | 10
3245 | 4 | 1000 | HGD-1002 | XA-1014 |  |  | Fault | ESBR-HS-CAF-0004 | DI | IS | LFAP |  | I | CCR | XA-1014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3246 | 2 | 1000 | UK-1001 | UK-1001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3247 | 2 | 1000 | UK-1001 | UK-1001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3248 | 2 | 1000 | UK-1001 | UK-1001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3249 | 4 | 1000 | UL-1001 | UL-1001A | OUTSIDE BATTERY ROOM | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3250 | 4 | 1000 | UL-1001 | UL-1001B | OUTSIDE BATTERY ROOM | Clean Agent System,MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3251 | 4 | 1000 | UL-1001 | UL-1001C | OUTSIDE BATTERY ROOM | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3252 | 2 | 1000 | UK-1002 | UK-1002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3253 | 2 | 1000 | UK-1002 | UK-1002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3254 | 2 | 1000 | UK-1002 | UK-1002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3255 | 4 | 1000 | UL-1002 | UL-1002A | OUTSIDE STAFF ROOM (FOR LAB.) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3256 | 4 | 1000 | UL-1002 | UL-1002B | OUTSIDE STAFF ROOM (FOR LAB.) | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3257 | 4 | 1000 | UL-1002 | UL-1002C | OUTSIDE STAFF ROOM (FOR LAB.) | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3258 | 2 | 1000 | UK-1003 | UK-1003A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3259 | 2 | 1000 | UK-1003 | UK-1003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3260 | 2 | 1000 | UK-1003 | UK-1003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3261 | 4 | 1000 | UL-1003 | UL-1003A | OUTSIDE HVAC | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3262 | 4 | 1000 | UL-1003 | UL-1003B | OUTSIDE HVAC | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3263 | 4 | 1000 | UL-1003 | UL-1003C | OUTSIDE HVAC | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3264 | 2 | 1000 | UK-1004 | UK-1004A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3265 | 2 | 1000 | UK-1004 | UK-1004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3266 | 2 | 1000 | UK-1004 | UK-1004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3267 | 4 | 1000 | UL-1004 | UL-1004A | MAIN ENTRY | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3268 | 4 | 1000 | UL-1004 | UL-1004B | MAIN ENTRY | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3269 | 4 | 1000 | UL-1004 | UL-1004C | MAIN ENTRY | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3270 | 2 | 1000 | UK-1005 | UK-1005A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3271 | 2 | 1000 | UK-1005 | UK-1005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3272 | 2 | 1000 | UK-1005 | UK-1005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3273 | 4 | 1000 | UL-1005 | UL-1005A | OUTSID UPS ROOM | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3274 | 4 | 1000 | UL-1005 | UL-1005B | OUTSID UPS ROOM | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3275 | 4 | 1000 | UL-1005 | UL-1005C | OUTSID UPS ROOM | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3276 | 2 | 1000 | UK-1006 | UK-1006A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3277 | 2 | 1000 | UK-1006 | UK-1006B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3278 | 2 | 1000 | UK-1006 | UK-1006C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3279 | 4 | 1000 | UL-1006 | UL-1006A | CORRIDOR | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3280 | 4 | 1000 | UL-1006 | UL-1006B | CORRIDOR | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3281 | 4 | 1000 | UL-1006 | UL-1006C | CORRIDOR | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND75 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3282 | 2 | 1000 | UK-1007 | UK-1007A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3283 | 2 | 1000 | UK-1007 | UK-1007B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3284 | 2 | 1000 | UK-1007 | UK-1007C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3285 | 4 | 1000 | UL-1007 | UL-1007A | CORRIDOR | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3286 | 4 | 1000 | UL-1007 | UL-1007B | CORRIDOR | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3287 | 4 | 1000 | UL-1007 | UL-1007C | CORRIDOR | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | d | CCR | 1000JND76 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3288 | 2 | 1000 | UK-1008 | UK-1008A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | SF | CCR | UK-1008 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3289 | 2 | 1000 | UK-1008 | UK-1008B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | SF | CCR | UK-1008 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3290 | 2 | 1000 | UK-1008 | UK-1008C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0009 | DO | NIS | LFAP |  | SF | CCR | UK-1008 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3291 | 3 | 1000 | EWSD-1001 | EWSAH-10011 | Activation Clean agent Main | On Hold | Early warning smoke detector | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | CCR | 1000JND77 | 1 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3292 | 3 | 1000 | EWSD-1001 | EWSAH-10012 | Activation of clean agent False Floor | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | CCR | 1000JND77 | 2 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3293 | 3 | 1000 | EWSD-1001 | EWSA-1001 | System Fault | On Hold |  | ESBR-HS-LYT-0008 | DIR | NIS | LFAP |  | d | CCR | 1000JND77 | 3 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3294 | 1 | 1000 | EWSD-1000 | EWSA-1000 | Alarm from FAP to FGS | On Hold |  | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3295 | 2 | 1000 | EWSD-1000 | EWXF-1000 | Fault Signal |  |  | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3296 | 1 | 1000 | CLA-1000 | YS-Y1000 | Clean Agent |  | Lockoff switch closed Control Room | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | Package inter cable connection , signals are not finalised
3297 | 1 | 1000 | CLA-1000 | YS-Y1002 |  |  | Lockoff switch closed Rack Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-1000A | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3298 | 1 | 1000 | CLA-1000 | YS-Y1003 |  |  | Lockoff switch closed EngineeringRoom | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-1000A | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3299 | 2 | 1000 | CLA-1000 | XS-Y1001 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT RACK ROOM OR IT'S FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3300 | 2 | 1000 | CLA-1000 | XS-Y1002 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3301 | 2 | 1000 | CLA-1000 | XS-Y1003 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT ENGINEERING ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3302 | 2 | 1000 | CLA-1000 | XL-Y1001 |  |  | DEACTIVATION OF CLEAN AGENT RACK ROOM OR IT'S FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3303 | 2 | 1000 | CLA-1000 | XL-Y1002 |  |  | DEACTIVATION OF CLEAN AGENT RACK ROOM OR IT'S FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3304 | 2 | 1000 | CLA-1000 | XL-Y1003 |  |  | DEACTIVATION OF CLEAN AGENT ENGINEERING ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3305 | 2 | 1000 | CLA-1000 | CSS-Y1011 |  |  | Clean Agent (auto Mode)RACK ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3306 | 2 | 1000 | CLA-1000 | CSS-Y1012 |  |  | Clean agent (Manule Mode)RACK ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3307 | 2 | 1000 | CLA-1000 | CSS-Y1013 |  |  | Clean Agent (Inhibit Mode)RACK ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3308 | 2 | 1000 | CLA-1000 | CSS-Y1021 |  |  | Clean Agent (auto Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 13 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3309 | 2 | 1000 | CLA-1000 | CSS-Y1022 |  |  | Clean agent (Manule Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 14 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3310 | 2 | 1000 | CLA-1000 | CSS-Y1023 |  |  | Clean Agent (Inhibit Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000A | 15 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3311 | 2 | 1000 | CLA-1000 | CSS-Y1031 |  |  | Clean Agent (auto Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3312 | 2 | 1000 | CLA-1000 | CSS-Y1032 |  |  | Clean agent (Manule Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3313 | 2 | 1000 | CLA-1000 | CSS-Y1033 |  |  | Clean Agent (Inhibit Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3314 | 2 | 1000 | CLA-1000 | CSS-Y1041 |  |  | Clean Agent (auto Mode)ENGINEERING ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3315 | 2 | 1000 | CLA-1000 | CSS-Y1042 |  |  | Clean agent (Manule Mode)ENGINEERING ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3316 | 2 | 1000 | CLA-1000 | CSS-Y1043 |  |  | Clean Agent (Inhibit Mode)ENGINEERING ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3317 | 2 | 1000 | CLA-1000 | CSS-Y1051 |  |  | Clean Agent (auto Mode)ENGINEERING ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3318 | 2 | 1000 | CLA-1000 | CSS-Y1052 |  |  | Clean agent (Manule Mode)ENGINEERING ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3319 | 2 | 1000 | CLA-1000 | CSS-Y1053 |  |  | Clean Agent (Inhibit Mode)ENGINEERING ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3320 | 2 | 1000 | CLA-1000 | PAH-Y1000 |  |  | Clean agent activated | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3321 | 2 | 1000 | CLA-1000 | XS-Y1000 |  |  | Clean agent auto discharge Command | ESBR-HS-PID-0002 | DOR | NIS | LFAP |  |  | CCR | CLAP-1000B | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3322 | 2 | 1000 | CLA-1000 | CLXA-Y1000 |  |  | fault signal | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3323 | 2 | 1000 | CLA-1000 | WAL-1000 |  |  | Weight loss capsules | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-1000B | 13 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3324 | 2 | 1000 | CLA-1000 | SOV-Y1001 |  |  | Actuation of clean agent in Control Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-1000B | 14 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3325 | 2 | 1000 | CLA-1000 | SOV-Y1002 |  |  | Actuation of clean agent in Rack Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-1000B | 15 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3326 | 2 | 1000 | CLA-1000 | SOV-Y1003 |  |  | Actuation of clean agent in EngineeringRoom | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-1000B | 16 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3327 | 4 | 1000 | CLAP-1000 | CLXA-Y1003A | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3328 | 4 | 1000 | CLAP-1000 | CLCSA-Y1000A | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3329 | 4 | 1000 | CLAP-1000 | CLXA-Y1001A | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3330 | 4 | 1000 | CLAP-1000 | CLXA-Y1002A | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000A | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3331 | 4 | 1000 | CLAP-1000 | CLXA-Y1000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3332 | 4 | 1000 | CLAP-1000 | YSA-Y1000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3333 | 4 | 1000 | CLAP-1000 | WAL-Y1000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3334 | 3 | 1000 | EW-1001 | FSH-10751 | Safety Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | LFAP |  | SF | F | EW-1001 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3335 | 3 | 1000 | EW-1001 | FAH-10751 |  |  | Flow Alarm High | ESBR-HS-CAF-0004 | [5 empty] | OWS
3336 | 3 | 1000 | EW-1001 | FO-10751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
3337 | 3 | 1000 | EW-1002 | FSH-10752 | Safety Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | LFAP |  | SF | F | EW-1002 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1
3338 | 3 | 1000 | EW-1002 | FAH-10752 |  |  | Flow Alarm High | ESBR-HS-CAF-0004 | [5 empty] | OWS
3339 | 3 | 1000 | EW-1002 | FO-10752 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
3340 | 3 | 1000 | EW-1001 | FSH-10751A | Safety Eye wash |  | Flow switch High | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3341 | 3 | 1000 | EW-1002 | FSH-10752A | Safety Eye wash |  | Flow switch High | ESBR-HS-CAF-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-1000B | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2
3342 | 2 | 3000 | CLA-3000 | YS-Y3000 | Clean Agent |  | Lockoff switch closed Control Room | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | Package inter cable connection , signals are not finalised
3343 | 2 | 3000 | CLA-3000 | YS-Y3002 |  |  | Lockoff switch closed Control Room False floor | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-3000A | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3344 | 2 | 3000 | CLA-3000 | YS-Y3003 |  |  | Lockoff switch closed Rack Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-3000A | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3345 | 2 | 3000 | CLA-3000 | XS-Y3001 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3346 | 2 | 3000 | CLA-3000 | XS-Y3002 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT CONTROL ROOM FALSE FOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3347 | 2 | 3000 | CLA-3000 | XS-Y3003 |  |  | ACTIVATION OF CLEAN AGENT TOTAL FLOODING SYSTEM AT RACK ROOM AND IT'S FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3348 | 2 | 3000 | CLA-3000 | XL-Y3001 |  |  | Clean Agent deactivated Control Room | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3349 | 2 | 3000 | CLA-3000 | XL-Y3002 |  |  | Clean Agent deactivated Control Room False floor | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3350 | 2 | 3000 | CLA-3000 | XL-Y3003 |  |  | Clean Agentdeactivated Rack Room | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3351 | 2 | 3000 | CLA-3000 | CSS-Y3011 |  |  | Clean Agent (auto Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3352 | 2 | 3000 | CLA-3000 | CSS-Y3012 |  |  | Clean agent (Manule Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3353 | 2 | 3000 | CLA-3000 | CSS-Y3013 |  |  | Clean Agent (Inhibit Mode)CONTROL ROOM | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000A | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3354 | 2 | 3000 | CLA-3000 | CSS-Y3021 |  |  | Clean Agent (auto Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3355 | 2 | 3000 | CLA-3000 | CSS-Y3022 |  |  | Clean agent (Manule Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3356 | 2 | 3000 | CLA-3000 | CSS-Y3023 |  |  | Clean Agent (Inhibit Mode)CONTROL ROOM FALSE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3357 | 2 | 3000 | CLA-3000 | CSS-Y3031 |  |  | Clean Agent (auto Mode)RACK ROOM AND IT'S FLASE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3358 | 2 | 3000 | CLA-3000 | CSS-Y3032 |  |  | Clean agent (Manule Mode)RACK ROOM AND IT'S FLASE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 5 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3359 | 2 | 3000 | CLA-3000 | CSS-Y3033 |  |  | Clean Agent (Inhibit Mode)RACK ROOM AND IT'S FLASE FLOOR | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 6 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3360 | 2 | 3000 | CLA-3000 | PAH-Y3000 |  |  | Clean agent activated | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3361 | 2 | 3000 | CLA-3000 | XS-Y3000 |  |  | Clean agent auto discharge Command | ESBR-HS-PID-0002 | DOR | NIS | LFAP |  | d | CCR | CLAP-3000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3362 | 2 | 3000 | CLA-3000 | CLXA-Y3000 |  |  | fault signal | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3363 | 2 | 3000 | CLA-3000 | WAL-Y3000 |  |  | Weight loss capsules | ESBR-HS-PID-0002 | DIR | NIS | LFAP |  |  | CCR | CLAP-3000B | 10 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3364 | 2 | 3000 | CLA-3000 | SOV-Y3001 |  |  | Actuation of clean agent in Control Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-3000B | 11 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3365 | 2 | 3000 | CLA-3000 | SOV-Y3002 |  |  | Actuation of clean agent in Control Room False floor | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-3000B | 12 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3366 | 2 | 3000 | CLA-3000 | SOV-Y3003 |  |  | Actuation of clean agent in Rack Room | ESBR-HS-PID-0002 |  |  | LFAP |  |  | CCR | CLAP-3000B | 13 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN
3367 | 4 | 3000 | CLA-3000 | CLXA-Y3003A | Signal from FAP to FGS |  | CLEAN AGENT ACTIVATION STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000A | 1 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3368 | 4 | 3000 | CLA-3000 | CSA-Y3000A | Signal from FAP to FGS |  | CLEAN AGENT INHIBIT STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000A | 2 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3369 | 4 | 3000 | CLA-3000 | CLXA-Y3001A | Signal from FAP to FGS |  | CLEAN AGENT MANUAL ACTIVATION MODE STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000A | 3 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3370 | 4 | 3000 | CLA-3000 | CLXA-Y3002A | Signal from FAP to FGS |  | STATUS LAMP OF CLEAN AGENT MANUAL DEACTIVATION HAND SWITCH OF CONCERNED Area | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000A | 4 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3371 | 4 | 3000 | CLA-3000 | CLXA-Y3000A | Signal from FAP to FGS |  | FAULT STATUS LAMP | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 7 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3372 | 4 | 3000 | CLA-3000 | YSA-Y3000A | Signal from FAP to FGS |  | LOCK OFF VALVE CLOSED STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 8 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3373 | 4 | 3000 | CLA-3000 | WAL-Y3000A | Signal from FAP to FGS |  | CLEAN AGENT CLYLINDER PRESSURE LOSS STATUS LAMP OF CONCERNED AREA | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 9 | 16-P-1.50-11-NAR-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3374 | 2 | 3000 | IRGD-3001 | IRGD/P-3001 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0018 | AIR | NIS | LFAP |  | d | MCC | IRGD-3001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3375 | 2 | 3000 | IRGD-3001 | IRGAH-3001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0005 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
3376 | 2 | 3000 | IRGD-3001 | IRGAHH3001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0005 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
3377 | 2 | 3000 | IRGD-3001 | XA-3001 |  |  | Fault | ESBR-HS-CAF-0005 | DI | NIS | LFAP |  | d | MCC | XA-3001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3378 | 2 | 3000 | IRGD-3002 | IRGD/P-3002 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0018 | AIR | NIS | LFAP |  | d | MCC | IRGD-3002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3379 | 2 | 3000 | IRGD-3002 | IRGAH-3002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0005 | [5 empty] | MCC | [10 empty] | %LFL |  | 10 |  |  |  |  | ESBR-CI-DAS-0030
3380 | 2 | 3000 | IRGD-3002 | IRGAHH3002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0005 | [5 empty] | MCC | [10 empty] | %LFL | 25 | [5 empty] | ESBR-CI-DAS-0030
3381 | 2 | 3000 | IRGD-3002 | XA-3002 |  |  | Fault | ESBR-HS-CAF-0005 | DI | NIS | LFAP |  | d | MCC | XA-3002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-2 | ESBR-CI-DAS-0030
3382 | 2 | 3000 | TGD-3001 | TGD-3001 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0018 | AIR | NIS | LFAP |  | d | CCR | TGD-3001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3383 | 2 | 3000 | TGD-3001 | TGAH-3001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0005 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3384 | 2 | 3000 | TGD-3001 | TGAHH-3001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0005 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3385 | 2 | 3000 | TGD-3001 | XA-3003 |  |  | Fault | ESBR-HS-CAF-0005 | DI | NIS | LFAP |  | d | CCR | XA-3003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3386 | 2 | 3000 | TGD-3002 | TGD-3002 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0018 | AIR | NIS | LFAP |  | d | CCR | TGD-3002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3387 | 2 | 3000 | TGD-3002 | TGAH-3002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0005 | [5 empty] | CCR | [10 empty] | (TLV-TWA) |  | 50
3388 | 2 | 3000 | TGD-3002 | TGAHH-3002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0005 | [5 empty] | CCR | [10 empty] | (TLV-TWA) | 100
3389 | 2 | 3000 | TGD-3002 | XA-3004 |  |  | Fault | ESBR-HS-CAF-0005 | DI | NIS | LFAP |  | d | CCR | XA-3004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3390 | 3 | 3000 | MCP-3001 | MCP-3001 | Finishing Outdoor | Entrance | Manual Call point | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d* | FCR | 3000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3391 | 3 | 3000 | MCP-3002 | MCP-3002 | Finishing Outdoor | Exit | Manual Call point | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d* | FCR | 3000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3392 | 3 | 3000 | MCP-3003 | MCP-3003 | Finishing Indoor | Control Room | Manual Call point | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d* | FCR | MCP-3003 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3393 | 2 | 3000 | UK-3001 | UK-3001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3394 | 2 | 3000 | UK-3001 | UK-3001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3395 | 2 | 3000 | UK-3001 | UK-3001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3396 | 4 | 3000 | UL-3001 | UL-3001A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | On Hold
3397 | 4 | 3000 | UL-3001 | UL-3001B | OUTSIDE BATTERY ROOM | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3398 | 4 | 3000 | UL-3001 | UL-3001C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | On Hold
3399 | 2 | 3000 | UK-3002 | UK-3002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3400 | 2 | 3000 | UK-3002 | UK-3002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3401 | 2 | 3000 | UK-3002 | UK-3002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3402 | 4 | 3000 | UL-3002 | UL-3002A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | On Hold
3403 | 4 | 3000 | UL-3002 | UL-3002B | OUTSIDE BATTERY ROOM | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3404 | 4 | 3000 | UL-3002 | UL-3002C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0018 | DO | NIS | LFAP |  | d | FCR | 3000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | On Hold
3405 | 3 | 3000 | EWSD-3001 | EWSA-3001 | Activation Clean agent Main | On Hold | Early warning smoke detector | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d | CCR | 3000JND73 | 1 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3406 | 3 | 3000 | EWSD-3001 | EWXA-3001 | Activation of clean agent False Floor | On Hold |  | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d | CCR | 3000JND73 | 2 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3407 | 3 | 3000 | EWSD-3001 | EWSA-3001 | System Fault | On Hold |  | ESBR-HS-LYT-0018 | DIR | NIS | LFAP |  | d | CCR | 3000JND73 | 3 | 08-P-1.50-11-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3408 | 2 | 3000 | EWSD-3000 | EWSA-3000 | Alarm from FAP to FGS | On Hold |  | ESBR-HS-CAF-0005 | DO | NIS | LFAP | FRR |  | FGDS | CAP-3000A | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3409 | 2 | 3000 | EWSD-3000 | EWXF-3000 | Fault Signal |  |  | ESBR-HS-CAF-0005 | DO | NIS | LFAP | FRR |  | FGDS | CAP-3000A | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3410 | 2 | 3000 | SD-3006 | SD-3006 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS | LFAP |  | SF | FCR | SD-3006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3411 | 2 | 3000 | SD-3006 | SD-3001 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3412 | 2 | 3000 | SD-3006 | SD-3002 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3413 | 2 | 3000 | SD-3006 | SD-3010 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 |  |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3414 | 2 | 3000 | SD-3006 | SD-3009 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 |  |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3415 | 2 | 3000 | SD-3006 | SD-3003 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3416 | 2 | 3000 | SD-3006 | SD-3004 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3417 | 2 | 3000 | SD-3006 | SD-3008 | CORRIDOR |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3418 | 2 | 3000 | SD-3006 | SD-3007 | OFFICE |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS |  |  | SF | FCR | SD-3007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3419 | 2 | 3000 | SD-3006 | SD-3005 | FIELD RACK ROOM |  | Smoke Detector | ESBR-HS-LYT-0018 | AL | NIS | LFAP |  | SF | FCR | SD-3005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3420 | 3 | 3000 | HVAC-3000 | MHKL-Y3000 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0005 | DOR | NIS | LFAP |  |  | FCR | HVAC3000 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3421 | 3 | 3000 | HVAC-3000 | XL-Y3000 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0005 | DIR | NIS | LFAP |  |  | FCR | HVAC3000 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3422 | 3 | 3000 | HVAC-3000 | HVAC-Y3000 | HVAC shutdown status from Panel |  | HVAC signals | ESBR-HS-CAF-0005 | DIR | NIS | LFAP |  |  | FCR | HVAC3000 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3423 | 2 | 3000 | HVAC-3000 | HVAC-3000A | HVAC shutdown on HVAC panel |  | HVAC signals to LFAP | ESBR-HS-CAF-0005 | DO | NIS | LFAP | CRR |  | FGDS | CAP-3000A | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3424 | 4 | 3000 | HVAC-3000 | XL-Y3001 | Operation Without Fault |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3425 | 4 | 3000 | HVAC-3000 | XL-Y3002 | Operation With Fault |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3426 | 4 | 3000 | HVAC-3000 | XL-Y3003 | Operation Stop due to Fault |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3427 | 4 | 3000 | HVAC-3000 | XL-Y3004 | MFD‐FLR‐001 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3428 | 4 | 3000 | HVAC-3000 | XL-Y3005 | MFD‐FLR‐002 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3429 | 4 | 3000 | HVAC-3000 | XL-Y3006 | MFD‐FLR‐003 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3430 | 4 | 3000 | HVAC-3000 | XL-Y3007 | MFD‐FLR‐004 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3431 | 4 | 3000 | HVAC-3000 | XL-Y3008 | MFD‐FLR‐005 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 11 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3432 | 4 | 3000 | HVAC-3000 | XL-Y3009 | FGD‐FLR‐001 status |  | HVAC signals to LFAP | ESBR‐HV‐PID‐1605 | DI | NIS | LFAP |  |  | FGDS | HVAC3000 | 12 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3433 | 2 | 3000 | IRGD-3000 | IRGA-3000 | Status signal to FGS |  |  | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3434 | 1 | 3000 | SD-3000 | SA-3000 | Status signal to FGS |  |  | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3435 | 2 | 3000 | TGD-3000 | TGA-3000 | Status signal to FGS |  |  | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3436 | 1 | 3000 | MCP-3000 | MCP-3000 | Status signal to FGS |  |  | ESBR-HS-CAF-0005 | DO | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3437 | 4 | 3000 | LFAP-3000 | LFXA-3000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3438 | 4 | 3000 | LFAP-3000 | LFXA-3000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-3000A | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3 | ESBR-CI-DAS-0030
3439 | 2 | 3000 | UK-3000 | UK-3000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3440 | 2 | 3000 | UK-3000 | UK-3000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3441 | 2 | 3000 | UK-3000 | UK-3000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3442 | 2 | 3000 | UL-3000 | UL-3000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3443 | 2 | 3000 | UL-3000 | UL-3000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3444 | 2 | 3000 | UL-3000 | UL-3000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-3000B | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-3
3445 | 2 | 3000 | EIS-3000 | EIS-3000 | Isolation of pewer supply | [5 empty] | LFAP | CRR |  | FGDS | EIS-3000 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3446 | 2 | 3000 | EIS-3001 | EIS-3001 | Isolation of Battery feaders | [5 empty] | LFAP | CRR |  | FGDS | EIS-3001 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3447 | 4 | 4000 | HVAC-4000 | MHKL-Y4001 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0007 | DOR | NIS | LFAP |  |  | CCR | HVAC4000 | 1 | 08-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3448 | 4 | 4000 | HVAC-4000 | MHKL-Y4002 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0007 | DOR | NIS | LFAP |  |  | CCR | HVAC4000 | 2 | 08-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3449 | 4 | 4000 | HVAC-4000 | XL-Y4001 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0007 | DIR | NIS | LFAP |  |  | CCR | HVAC4000 | 3 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3450 | 4 | 4000 | HVAC-4000 | XL-Y4002 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0007 | DIR | NIS | LFAP |  |  | CCR | HVAC4000 | 4 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3451 | 4 | 4000 | HVAC-4000 | HVAC-Y4001 |  |  | HVAC Shutdown singnal | ESBR-HS-CAF-0007 | DIR | NIS | LFAP |  |  | MW | HVAC4000 | 5 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3452 | 4 | 4000 | HVAC-4000 | HVAC-Y4002 |  |  | HVAC Shutdown singnal | ESBR-HS-CAF-0007 | DIR | NIS | LFAP |  |  | MW | HVAC4000 | 6 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3453 | 4 | 4000 | HVAC-4000 | HVAC-4000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0007 | DO | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3454 | 4 | 4000 | HVAC-4000 | HVAC-4002 | HVAC status |  | HVAC signals to FGS |  |  |  | LFAP | CRR |  | FGDS | CAP-4000 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3455 | 2 | 4000 | SD-4016 | SD-4016 | Mechanical Machine Workshop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | SD-4016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3456 | 2 | 4000 | SD-4016 | SD-4009 | Mechanical Machine Workshop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3457 | 2 | 4000 | SD-4016 | SD-4008 | Mechanical Machine Workshop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3458 | 2 | 4000 | SD-4016 | SD-4007 | Mechanical Machine Workshop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3459 | 2 | 4000 | SD-4016 | SD-4001 | Administrative |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3460 | 2 | 4000 | SD-4016 | SD-4002 | Inst. Engineers room |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3461 | 2 | 4000 | SD-4016 | SD-4003 | Mec. Engineers room |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3462 | 2 | 4000 | SD-4016 | SD-4004 | Elec. Engineers room |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3463 | 2 | 4000 | SD-4016 | SD-4005 | Managers Room |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3464 | 2 | 4000 | SD-4016 | HDROR-4001 | Pantery |  | Heat Detector Rate of Rise | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | HDROR-4001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3465 | 2 | 4000 | SD-4016 | SD-4006 | HVAC Room |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | SD-4006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3466 | 2 | 4000 | SD-4015 | SD-4015 | Corrosion Preperation |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | SD-4015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3467 | 2 | 4000 | SD-4015 | SD-4013 | Electrical Shop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3468 | 2 | 4000 | SD-4015 | SD-4011 | Instrument Shop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3469 | 2 | 4000 | SD-4015 | SD-4017 | Valve Shop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3470 | 2 | 4000 | SD-4015 | SD-4010 | Valve Shop |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3471 | 2 | 4000 | SD-4015 | SD-4012 | Instrument Satore |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | SD-4012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3472 | 2 | 4000 | SD-4015 | SD-4014 | Electrical Store |  | Smoke detector Above ceiling | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | SD-4014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3473 | 1 | 4000 | MCP-4009 | MCP-4009 | MW Indoor | HVAC Room | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | MCP-4009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3474 | 1 | 4000 | MCP-4009 | MCP-4010 | MW Indoor | Corridor | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3475 | 1 | 4000 | MCP-4009 | MCP-4008 | MW Indoor | Mechanical Machine Workshop | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3476 | 1 | 4000 | MCP-4009 | MCP-4011 | MW Indoor | Mechanical Machine Workshop | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3477 | 1 | 4000 | MCP-4009 | MCP-4016 | MW Indoor | Valve Shop | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3478 | 1 | 4000 | MCP-4009 | MCP-4012 | MW Indoor | Mechanical Machine Workshop | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3479 | 1 | 4000 | MCP-4009 | MCP-4015 | MW Indoor | Corrosion Preperation | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3480 | 1 | 4000 | MCP-4009 | MCP-4014 | MW Indoor | Welding and Pipe fabrication Area | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS |  |  | SF | MW | MCP-4014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3481 | 1 | 4000 | MCP-4009 | MCP-4013 | MW Indoor | Mechanical Machine Workshop | Manual Call Point Inside Building | ESBR-HS-LYT-0007 | AL | NIS | LFAP |  | SF | MW | MCP-4013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3482 | 3 | 4000 | MCP-4002 | MCP-4002 | MW Outdoor | Red Flashing Light | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3483 | 3 | 4000 | MCP-4001 | MCP-4001 | MW Outdoor |  | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3484 | 3 | 4000 | MCP-4007 | MCP-4007 | MW Outdoor |  | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND76 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3485 | 3 | 4000 | MCP-4006 | MCP-4006 | MW Outdoor |  | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND75 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3486 | 3 | 4000 | MCP-4005 | MCP-4005 | MW Outdoor |  | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND74 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3487 | 3 | 4000 | MCP-4004 | MCP-4004 | MW Outdoor |  | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3488 | 3 | 4000 | MCP-4003 | MCP-4003 | MW Outdoor | AUDIBLE ALARM (CONTINUOUS ) | Manual Call Point Outside Building | ESBR-HS-LYT-0007 | DIR | NIS | LFAP |  | d | MW | 4000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3489 | 2 | 4000 | IRGD-4001 | IRGD/P-4001 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | IRGD-4001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3490 | 1 | 4000 | IRGD-4001 | IRGAH-4001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL |  | 10
3491 | 1 | 4000 | IRGD-4001 | IRGAHH4001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL | 25
3492 | 2 | 4000 | IRGD-4001 | XA-4001 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3493 | 2 | 4000 | IRGD-4002 | IRGD/P-4002 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | IRGD-4002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3494 | 1 | 4000 | IRGD-4002 | IRGAH-4002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL |  | 10
3495 | 1 | 4000 | IRGD-4002 | IRGAHH4002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL | 25
3496 | 2 | 4000 | IRGD-4002 | XA-4002 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3497 | 2 | 4000 | IRGD-4003 | IRGD/P-4003 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | IRGD-4003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3498 | 1 | 4000 | IRGD-4003 | IRGAH-4003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL |  | 10
3499 | 1 | 4000 | IRGD-4003 | IRGAHH4003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL | 25
3500 | 2 | 4000 | IRGD-4003 | XA-4003 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3501 | 2 | 4000 | IRGD-4004 | IRGD/P-4004 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | IRGD-4004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3502 | 2 | 4000 | IRGD-4004 | IRGAH-4004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL |  | 10
3503 | 2 | 4000 | IRGD-4004 | IRGAHH4004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL | 25
3504 | 2 | 4000 | IRGD-4004 | XA-4009 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3505 | 2 | 4000 | IRGD-4005 | IRGD/P-4005 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | IRGD-4005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3506 | 2 | 4000 | IRGD-4005 | IRGAH-4005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL |  | 10
3507 | 2 | 4000 | IRGD-4005 | IRGAHH4005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | %LFL | 25
3508 | 2 | 4000 | IRGD-4005 | XA-4010 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3509 | 2 | 4000 | TGD-4001 | TGD-4001 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | TGD-4001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3510 | 1 | 4000 | TGD-4001 | TGAH-4001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) |  | 50
3511 | 1 | 4000 | TGD-4001 | TGAHH-4001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) | 100
3512 | 2 | 4000 | TGD-4001 | XA-4004 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3513 | 2 | 4000 | TGD-4002 | TGD-4002 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | TGD-4002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3514 | 1 | 4000 | TGD-4002 | TGAH-4002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) |  | 50
3515 | 1 | 4000 | TGD-4002 | TGAHH-4002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) | 100
3516 | 2 | 4000 | TGD-4002 | XA-4005 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3517 | 2 | 4000 | TGD-4003 | TGD-4003 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | TGD-4003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3518 | 1 | 4000 | TGD-4003 | TGAH-4003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) |  | 50
3519 | 1 | 4000 | TGD-4003 | TGAHH-4003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) | 100
3520 | 2 | 4000 | TGD-4003 | XA-4006 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3521 | 2 | 4000 | TGD-4004 | TGD-4004 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | TGD-4004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3522 | 2 | 4000 | TGD-4004 | TGAH-4004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) |  | 50
3523 | 2 | 4000 | TGD-4004 | TGAHH-4004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) | 100
3524 | 2 | 4000 | TGD-4004 | XA-4011 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3525 | 2 | 4000 | TGD-4005 | TGD-4005 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0007 | AIR | NIS | LFAP |  | d | MW | TGD-4005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3526 | 2 | 4000 | TGD-4005 | TGAH-4005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) |  | 50
3527 | 2 | 4000 | TGD-4005 | TGAHH-4005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0007 | [5 empty] | MW | [10 empty] | (TLV-TWA) | 100
3528 | 2 | 4000 | TGD-4005 | XA-4012 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3529 | 2 | 4000 | FD-4001 | FD-4001 | DIESEL GENERATOR ROOM |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-0007 | AI | NIS | LFAP |  | d | MW | FD-4001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3530 | 1 | 4000 | FD-4001 | FAH-4001 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0007
3531 | 2 | 4000 | FD-4001 | XA-4007 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MW | XA-4007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3532 | 2 | 4000 | FD-4002 | FD-4002 | DIESEL GENERATOR ROOM |  | FLAME DETECTION IN OPEN AREA | ESBR-HS-LYT-0007 | AI | NIS | LFAP |  | d | MCC | FD-4002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3533 | 1 | 4000 | FD-4002 | FAH-4002 | (RED FLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) | Flame Alarm High | ESBR-HS-CAF-0007
3534 | 2 | 4000 | FD-4002 | XA-4008 |  |  | Fault | ESBR-HS-CAF-0007 | DI | NIS | LFAP |  | d | MCC | XA-4008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3535 | 2 | 4000 | UK-4001 | UK-4001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3536 | 2 | 4000 | UK-4001 | UK-4001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3537 | 2 | 4000 | UK-4001 | UK-4001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3538 | 4 | 4000 | UL-4001 | UL-4001A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3539 | 4 | 4000 | UL-4001 | UL-4001B |  | Clean Agent System,MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3540 | 4 | 4000 | UL-4001 | UL-4001C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3541 | 2 | 4000 | UK-4002 | UK-4002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3542 | 2 | 4000 | UK-4002 | UK-4002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3543 | 2 | 4000 | UK-4002 | UK-4002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3544 | 4 | 4000 | UL-4002 | UL-4002A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3545 | 4 | 4000 | UL-4002 | UL-4002B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3546 | 4 | 4000 | UL-4002 | UL-4002C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3547 | 2 | 4000 | UK-4003 | UK-4003A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3548 | 2 | 4000 | UK-4003 | UK-4003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3549 | 2 | 4000 | UK-4003 | UK-4003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3550 | 4 | 4000 | UL-4003 | UL-4003A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3551 | 4 | 4000 | UL-4003 | UL-4003B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3552 | 4 | 4000 | UL-4003 | UL-4003C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3553 | 2 | 4000 | UK-4004 | UK-4004A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3554 | 2 | 4000 | UK-4004 | UK-4004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3555 | 2 | 4000 | UK-4004 | UK-4004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3556 | 4 | 4000 | UL-4004 | UL-4004A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3557 | 4 | 4000 | UL-4004 | UL-4004B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3558 | 4 | 4000 | UL-4004 | UL-4004C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3559 | 2 | 4000 | UK-4005 | UK-4005A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3560 | 2 | 4000 | UK-4005 | UK-4005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3561 | 2 | 4000 | UK-4005 | UK-4005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3562 | 4 | 4000 | UL-4005 | UL-4005A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3563 | 4 | 4000 | UL-4005 | UL-4005B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3564 | 4 | 4000 | UL-4005 | UL-4005C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3565 | 2 | 4000 | UK-4006 | UK-4006A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3566 | 2 | 4000 | UK-4006 | UK-4006B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3567 | 2 | 4000 | UK-4006 | UK-4006C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3568 | 4 | 4000 | UL-4006 | UL-4006A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3569 | 4 | 4000 | UL-4006 | UL-4006B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3570 | 4 | 4000 | UL-4006 | UL-4006C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND75 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3571 | 2 | 4000 | UK-4007 | UK-4007A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3572 | 2 | 4000 | UK-4007 | UK-4007B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3573 | 2 | 4000 | UK-4007 | UK-4007C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3574 | 4 | 4000 | UL-4007 | UL-4007A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3575 | 4 | 4000 | UL-4007 | UL-4007B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3576 | 4 | 4000 | UL-4007 | UL-4007C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | d | MW | 4000JND76 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | On Hold
3577 | 2 | 4000 | UK-4008 | UK-4008B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | SF | MW | Uk-4008 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3578 | 2 | 4000 | UK-4008 | UK-4008C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | SF | MW | Uk-4008 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3579 | 2 | 4000 | UK-4008 | UK-4008A | not used | MCP/Fire |  | ESBR-HS-LYT-0007 | DO | NIS | LFAP |  | SF | MW | Uk-4008 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3580 | 3 | 4000 | FD-4000 | FA-4000 | Status signal to FGS |  |  | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3581 | 3 | 4000 | SD-4000 | SA-4000 | Status signal to FGS |  |  | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3582 | 3 | 4000 | TGD-4000 | TGA-4000 | Status signal to FGS |  |  | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3583 | 3 | 4000 | MCP-4000 | MCP-4000 | Status signal to FGS |  |  | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3584 | 3 | 4000 | IRGD-4000 | IRGA-4000 | Status signal to FGS |  |  | ESBR-HS-CAF-0007 | DO | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3585 | 4 | 4000 | LFAP-4000 | LFXF-4000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3586 | 4 | 4000 | LFAP-4000 | LFXA-4000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-4000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3587 | 3 | 4000 | EW-3001 | FSH-30751 | Safety Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | LFAP |  | SF | F | EW-3001 | 2 | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3588 | 3 | 4000 | EW-3001 | FAH-30751 |  |  | Flow Alarm High | ESBR-HS-UDD-0005 | [5 empty] | OWS
3589 | 3 | 4000 | EW-3001 | FO-30751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
3590 | 3 | 4000 | EW-3001 | FSH-30751A | Safety Eye wash |  | Flow switch High | ESBR-HS-CAF-0007 | DO | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | [10 empty] | ESBR-CI-DWG-0002-4
3591 | 3 | 4000 | UK-4000 | UK-4000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3592 | 3 | 4000 | UK-4000 | UK-4000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3593 | 3 | 4000 | UK-4000 | UK-4000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3594 | 3 | 4000 | UL-4000 | UL-4000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3595 | 3 | 4000 | UL-4000 | UL-4000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3596 | 3 | 4000 | UL-4000 | UL-4000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-4000 | 15 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3597 | 2 | 4000 | EIS-4000 | EIS-4000 | Isolation of pewer supply | [5 empty] | LFAP | CRR |  | FGDS | EIS-4000 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3598 | 2 | 4000 | EIS-4001 | EIS-4001 | Isolation of Battery feaders | [5 empty] | LFAP | CRR |  | FGDS | EIS-4001 | 1 | 01-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | Close | [13 empty] | Shall be looked at and revised
3599 | 3 | 5000 | SD-5000 | SA-5000 | Status signal to FGS |  |  | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3600 | 3 | 5000 | TGD-5000 | TGA-5000 | Status signal to FGS |  |  | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3601 | 3 | 5000 | MCP-5000 | MCP-5000 | Status signal to FGS |  |  | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3602 | 3 | 5000 | IRGD-5000 | IRGA-5000 | Status signal to FGS |  |  | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3603 | 3 | 5000 | SDOP-5000 | SAOP-5000 | Status signal to FGS |  |  | ESBR-HS-CAF-0008 | DO | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3604 | 3 | 5000 | PSH-5750 | PSH-5750 | Pressure switch |  | Pressure signal high for warehouse sprinkler system | ESBR-HS-PID-0004 | DOR | NIS | LFAP |  |  | WH | CAP-5000 |  | 01-P-1.50-01-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
3605 | 3 | 5000 | PSH-5750 | PSH-5750A | Status signal to FGS |  | Pressure signal high for warehouse sprinkler system | ESBR-HS-PID-0004 | DO | NIS | LFAP | CRR |  | FGDS | CAP-5000 |  | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN
3606 | 4 | 5000 | LFAP-5000 | LFXF-5000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3607 | 4 | 5000 | LFAP-5000 | LFXA-5000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-5000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3608 | 3 | 5000 | EW-4001 | FSH-40751 | Safety Eye wash |  | Flow switch High | ESBR-HS-UDD-0005 | DI | NIS | LFAP |  | SF | F | EW-4001 | 2 | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4
3609 | 3 | 5000 | EW-4001 | FAH-40751 |  |  | Flow Alarm High | ESBR-HS-CAF-0008 | [5 empty] | OWS
3610 | 3 | 5000 | EW-4001 | FO-40751 | Safety Eye wash |  | Flow element | ESBR-HS-UDD-0005 | [5 empty] | F
3611 | 3 | 5000 | EW-4001 | FSH-40751A | Safety Eye wash |  | Flow switch High | ESBR-HS-CAF-0008 | DO | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 15 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | [10 empty] | ESBR-CI-DWG-0002-5
3612 | 3 | 5000 | UK-5000 | UK-5000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3613 | 3 | 5000 | UK-5000 | UK-5000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3614 | 3 | 5000 | UK-5000 | UK-5000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3615 | 3 | 5000 | UL-5000 | UL-5000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3616 | 3 | 5000 | UL-5000 | UL-5000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3617 | 3 | 5000 | UL-5000 | UL-5000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5
3618 | 2 | 5000 | HDROR-5001 | HDROR-5001 | WH Indoor |  | Combined Smoke and Heat detector | ESBR-HS-LYT-0022 | AL | NIS | LFAP |  | SF | WH | HD-5001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3619 | 2 | 5000 | HDROR-5001 | SD-5017 | WH Indoor |  | Combined Smoke and Heat detector | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | SD-5017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3620 | 2 | 5000 | HDROR-5001 | SD-5003 | WH Indoor |  | Combined Smoke and Heat detector | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | SD-5003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3621 | 2 | 5000 | HDROR-5001 | SD-5001 | WH Indoor |  | Combined Smoke and Heat detector | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | SD-5001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3622 | 2 | 5000 | HDROR-5001 | SD-5002 | WH Indoor |  | Combined Smoke and Heat detector | ESBR-HS-LYT-0022 | AL | NIS | LFAP |  | SF | WH | SD-5002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3623 | 1 | 5000 | SD-5004 | SD/OPT-5004 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3624 | 2 | 5000 | SD-5004 | SD/OPR-5004 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5004 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3625 | 1 | 5000 | SD-5004 | SAH-5004 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3626 | 2 | 5000 | SD-5004 | XA-5004 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5004 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3627 | 1 | 5000 | SD-5005 | SD/OPT-5005 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3628 | 2 | 5000 | SD-5005 | SD/OPR-5005 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5005 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3629 | 1 | 5000 | SD-5005 | SAH-5005 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3630 | 2 | 5000 | SD-5005 | XA-5005 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5005 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3631 | 1 | 5000 | SD-5006 | SD/OPT-5006 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3632 | 2 | 5000 | SD-5006 | SD/OPR-5006 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5006 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3633 | 1 | 5000 | SD-5006 | SAH-5006 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3634 | 2 | 5000 | SD-5006 | XA-5006 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5006 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3635 | 1 | 5000 | SD-5007 | SD/OPT-5007 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3636 | 2 | 5000 | SD-5007 | SD/OPR-5007 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5007 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3637 | 1 | 5000 | SD-5007 | SAH-5007 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3638 | 2 | 5000 | SD-5007 | XA-5007 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5007 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3639 | 1 | 5000 | SD-5008 | SD/OPT-5008 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3640 | 2 | 5000 | SD-5008 | SD/OPR-5008 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5008 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3641 | 1 | 5000 | SD-5008 | SAH-5008 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3642 | 2 | 5000 | SD-5008 | XA-5008 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5008 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3643 | 1 | 5000 | SD-5009 | SD/OPT-5009 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3644 | 2 | 5000 | SD-5009 | SD/OPR-5009 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5009 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3645 | 1 | 5000 | SD-5009 | SAH-5009 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3646 | 2 | 5000 | SD-5009 | XA-5009 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5009 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3647 | 1 | 5000 | SD-5010 | SD/OPT-5010 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3648 | 2 | 5000 | SD-5010 | SD/OPR-5010 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5010 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3649 | 1 | 5000 | SD-5010 | SAH-5010 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3650 | 2 | 5000 | SD-5010 | XA-5010 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5010 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3651 | 1 | 5000 | SD-5011 | SD/OPT-5011 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3652 | 2 | 5000 | SD-5011 | SD/OPR-5011 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5011 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3653 | 1 | 5000 | SD-5011 | SAH-5011 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3654 | 2 | 5000 | SD-5011 | XA-5011 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5011 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3655 | 1 | 5000 | SD-5012 | SD/OPT-5012 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3656 | 2 | 5000 | SD-5012 | SD/OPR-5012 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5012 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3657 | 1 | 5000 | SD-5012 | SAH-5012 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3658 | 2 | 5000 | SD-5012 | XA-5012 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5012 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3659 | 1 | 5000 | SD-5013 | SD/OPT-5013 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3660 | 2 | 5000 | SD-5013 | SD/OPR-5013 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5013 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3661 | 1 | 5000 | SD-5013 | SAH-5013 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3662 | 2 | 5000 | SD-5013 | XA-5013 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5013 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3663 | 1 | 5000 | SD-5014 | SD/OPT-5014 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3664 | 2 | 5000 | SD-5014 | SD/OPR-5014 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5014 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3665 | 1 | 5000 | SD-5014 | SAH-5014 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3666 | 2 | 5000 | SD-5014 | XA-5014 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5014 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3667 | 1 | 5000 | SD-5015 | SD/OPT-5015 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3668 | 2 | 5000 | SD-5015 | SD/OPR-5015 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5015 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3669 | 1 | 5000 | SD-5015 | SAH-5015 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008
3670 | 2 | 5000 | SD-5015 | XA-5015 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5015 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3671 | 1 | 5000 | SD-5016 | SD/OPT-5016 |  | Open Path Type Smoke Detector Transmitter | Smoke (Open Area) | ESBR-HS-LYT-0022 | [5 empty] | WH
3672 | 2 | 5000 | SD-5016 | SD/OPR-5016 |  | Open Path Type Smoke Detector Reciever | Smoke (Open Area) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | SF | WH | SD-5016 |  | 01-T-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3673 | 1 | 5000 | SD-5016 | SAH-5016 | (RedFLASHING LIGHT) | AUDIBLE ALARM (CONTINUOUS ) |  | ESBR-HS-CAF-0008 | [5 empty] | WH
3674 | 2 | 5000 | SD-5016 | XA-5016 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5016 |  | 01-P-1.50-01-NAR-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3675 | 2 | 5000 | IRGD-5001 | IRGD/P-5001 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | IRGD-5001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3676 | 1 | 5000 | IRGD-5001 | IRGAH-5001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL |  | 10
3677 | 1 | 5000 | IRGD-5001 | IRGAHH5001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL | 25
3678 | 2 | 5000 | IRGD-5001 | XA-5001 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3679 | 2 | 5000 | IRGD-5002 | IRGD/P-5002 | HVAC Inside Duct | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | IRGD-5002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3680 | 2 | 5000 | IRGD-5002 | IRGAH-5002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL |  | 10
3681 | 2 | 5000 | IRGD-5002 | IRGAHH5002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL | 25
3682 | 2 | 5000 | IRGD-5002 | XA-5017 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3683 | 2 | 5000 | IRGD-5003 | IRGD/P-5003 | HVAC Inside Duct | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | IRGD-5003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3684 | 2 | 5000 | IRGD-5003 | IRGAH-5003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL |  | 10
3685 | 2 | 5000 | IRGD-5003 | IRGAHH5003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | %LFL | 25
3686 | 2 | 5000 | IRGD-5003 | XA-5018 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3687 | 2 | 5000 | TGD-5001 | TGD-5001 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | TGD-5001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3688 | 1 | 5000 | TGD-5001 | TGAH-5001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) |  | 50
3689 | 1 | 5000 | TGD-5001 | TGAHH-5001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) | 100
3690 | 2 | 5000 | TGD-5001 | XA-5002 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3691 | 2 | 5000 | TGD-5002 | TGD-5002 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | TGD-5002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3692 | 2 | 5000 | TGD-5002 | TGAH-5002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) |  | 50
3693 | 2 | 5000 | TGD-5002 | TGAHH-5002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) | 100
3694 | 2 | 5000 | TGD-5002 | XA-5019 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5019 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3695 | 2 | 5000 | TGD-5003 | TGD-5003 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0022 | AIR | NIS | LFAP |  | d | WH | TGD-5003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3696 | 2 | 5000 | TGD-5003 | TGAH-5003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) |  | 50
3697 | 2 | 5000 | TGD-5003 | TGAHH-5003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0008 | [5 empty] | WH | [10 empty] | (TLV-TWA) | 100
3698 | 2 | 5000 | TGD-5003 | XA-5020 |  |  | Fault | ESBR-HS-CAF-0008 | DI | NIS | LFAP |  | d | WH | XA-5020 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3699 | 1 | 5000 | MCP-5011 | MCP-5011 | WH Indoor | Red Flashing Light | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS | LFAP |  | SF | WH | MCP-5011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | F&G device loops are subject to change due to area classification of areas with in the compound, that cause the use of alternative devices with regard to area classification
3700 | 1 | 5000 | MCP-5011 | MCP-5008 | WH Indoor |  | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | MCP-5008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3701 | 1 | 5000 | MCP-5011 | MCP-5006 | WH Indoor |  | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | MCP-5006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3702 | 1 | 5000 | MCP-5011 | MCP-5007 | WH Indoor |  | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | MCP-5007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3703 | 1 | 5000 | MCP-5011 | MCP-5009 | WH Indoor |  | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS |  |  | SF | WH | MCP-5009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3704 | 1 | 5000 | MCP-5011 | MCP-5010 | WH Indoor | AUDIBLE ALARM (CONTINUOUS ) | Manual Call Point Inside | ESBR-HS-LYT-0022 | AL | NIS | LFAP |  | SF | WH | MCP-5010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3705 | 3 | 5000 | MCP-5004 | MCP-5004 | WH Outdoor | Red Flashing Light | Manual Call Point Outside | ESBR-HS-LYT-0022 | DIR | NIS | LFAP |  | d | WH | 5000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3706 | 3 | 5000 | MCP-5005 | MCP-5005 | WH Outdoor |  | Manual Call Point Outside | ESBR-HS-LYT-0022 | DIR | NIS | LFAP |  | d | WH | 5000JND74 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3707 | 3 | 5000 | MCP-5001 | MCP-5001 | WH Outdoor |  | Manual Call Point Outside | ESBR-HS-LYT-0022 | DIR | NIS | LFAP |  | d | WH | 5000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3708 | 3 | 5000 | MCP-5002 | MCP-5002 | WH Outdoor |  | Manual Call Point Outside | ESBR-HS-LYT-0022 | DIR | NIS | LFAP |  | d | WH | 5000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3709 | 3 | 5000 | MCP-5003 | MCP-5003 | WH Outdoor | AUDIBLE ALARM (CONTINUOUS ) | Manual Call Point Outside | ESBR-HS-LYT-0022 | DIR | NIS | LFAP |  | d | WH | 5000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3710 | 2 | 5000 | UK-5001 | UK-5001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3711 | 2 | 5000 | UK-5001 | UK-5001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3712 | 2 | 5000 | UK-5001 | UK-5001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3713 | 4 | 5000 | UL-5001 | UL-5001A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3714 | 4 | 5000 | UL-5001 | UL-5001B |  | Clean Agent System,MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3715 | 4 | 5000 | UL-5001 | UL-5001C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3716 | 2 | 5000 | UK-5002 | UK-5002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3717 | 2 | 5000 | UK-5002 | UK-5002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3718 | 2 | 5000 | UK-5002 | UK-5002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3719 | 4 | 5000 | UL-5002 | UL-5002A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3720 | 4 | 5000 | UL-5002 | UL-5002B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3721 | 4 | 5000 | UL-5002 | UL-5002C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3722 | 2 | 5000 | UK-5003 | UK-5003A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3723 | 2 | 5000 | UK-5003 | UK-5003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3724 | 2 | 5000 | UK-5003 | UK-5003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3725 | 4 | 5000 | UL-5003 | UL-5003A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3726 | 4 | 5000 | UL-5003 | UL-5003B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3727 | 4 | 5000 | UL-5003 | UL-5003C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3728 | 2 | 5000 | UK-5004 | UK-5004A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3729 | 2 | 5000 | UK-5004 | UK-5004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3730 | 2 | 5000 | UK-5004 | UK-5004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0008 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3731 | 4 | 5000 | UL-5004 | UL-5004A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3732 | 4 | 5000 | UL-5004 | UL-5004B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3733 | 4 | 5000 | UL-5004 | UL-5004C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3734 | 2 | 5000 | UK-5005 | UK-5005A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3735 | 2 | 5000 | UK-5005 | UK-5005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3736 | 2 | 5000 | UK-5005 | UK-5005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3737 | 4 | 5000 | UL-5005 | UL-5005A | not used | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3738 | 4 | 5000 | UL-5005 | UL-5005B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3739 | 4 | 5000 | UL-5005 | UL-5005C | not used | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | d | WH | 5000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | On Hold
3740 | 2 | 5000 | UK-5006 | UK-5006B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5006 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3741 | 2 | 5000 | UK-5006 | UK-5006C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5006 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3742 | 2 | 5000 | UK-5006 | UK-5006A | not used | MCP/Fire |  | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5006 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3743 | 2 | 5000 | UK-5007 | UK-5007B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5007 | 1,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3744 | 2 | 5000 | UK-5007 | UK-5007C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5007 | 2,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3745 | 2 | 5000 | UK-5007 | UK-5007A | not used | MCP/Fire |  | ESBR-HS-LYT-0022 | DO | NIS | LFAP |  | SF | WH | UK-5007 | 3,3 | 04-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030
3746 | 4 | 5000 | HVAC-5000 | MHKL-Y5000 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0008 | DOR | NIS | LFAP |  |  | WH | HVAC5000 | 1 | 16-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3747 | 4 | 5000 | HVAC-5000 | XL-Y5000 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0008 | DIR | NIS | LFAP |  |  | WH | HVAC5000 | 2 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3748 | 4 | 5000 | HVAC-5000 | HVAC-Y5000 |  |  | HVAC Shutdown singnal | ESBR-HS-CAF-0008 | DIR | NIS | LFAP |  |  | WH | HVAC5000 | 3 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3749 | 4 | 5000 | HVAC-5000 | HVAC-5000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0008 | DO | NIS | LFAP | CRR |  | FGDS | CAP-5000 | 8 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-5 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3750 | 4 | 5000 | HVAC-5000 | XL-Y5001 | Operation Without Fault |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 4 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3751 | 4 | 5000 | HVAC-5000 | XL-Y5002 | Operation With Fault |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 5 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3752 | 4 | 5000 | HVAC-5000 | XL-Y5003 | Operation Stop due to Fault |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 6 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3753 | 4 | 5000 | HVAC-5000 | XL-Y5004 | MFD‐WAR‐001 status |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 7 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3754 | 4 | 5000 | HVAC-5000 | XL-Y5005 | MFD‐WAR‐002 status |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 8 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3755 | 4 | 5000 | HVAC-5000 | XL-Y5006 | MFD‐WAR‐003 status |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 9 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3756 | 4 | 5000 | HVAC-5000 | XL-Y5007 | FGS-WAR-001 Status |  | HVAC signal to LFAP | ESBR‐HV‐PID‐0002 | DI | NIS | LFAP |  |  | WH | HVAC5000 | 10 | 16-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [13 empty] | ON HOLD, Signals will be modified based on vendor data
3757 | 3 | 7000 | IRGD-7001 | IRGD/P-7001 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3758 | 3 | 7000 | IRGD-7001 | IRGAH-7001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3759 | 3 | 7000 | IRGD-7001 | IRGAHH7001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3760 | 3 | 7000 | IRGD-7001 | XA-7001 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3761 | 3 | 7000 | IRGD-7002 | IRGD/P-7002 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3762 | 3 | 7000 | IRGD-7002 | IRGAH-7002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3763 | 3 | 7000 | IRGD-7002 | IRGAHH7002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3764 | 3 | 7000 | IRGD-7002 | XA-7002 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3765 | 3 | 7000 | IRGD-7003 | IRGD/P-7003 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3766 | 3 | 7000 | IRGD-7003 | IRGAH-7003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3767 | 3 | 7000 | IRGD-7003 | IRGAHH7003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3768 | 3 | 7000 | IRGD-7003 | XA-7003 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3769 | 3 | 7000 | IRGD-7004 | IRGD/P-7004 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3770 | 3 | 7000 | IRGD-7004 | IRGAH-7004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3771 | 3 | 7000 | IRGD-7004 | IRGAHH7004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3772 | 3 | 7000 | IRGD-7004 | XA-7004 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3773 | 4 | 7000 | IRGD-7005 | IRGD/P-7005 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3774 | 4 | 7000 | IRGD-7005 | IRGAH-7005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3775 | 4 | 7000 | IRGD-7005 | IRGAHH7005 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3776 | 4 | 7000 | IRGD-7005 | XA-7009 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3777 | 4 | 7000 | IRGD-7006 | IRGD/P-7006 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3778 | 4 | 7000 | IRGD-7006 | IRGAH-7006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3779 | 4 | 7000 | IRGD-7006 | IRGAHH7006 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3780 | 4 | 7000 | IRGD-7006 | XA-7010 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3781 | 4 | 7000 | IRGD-7007 | IRGD/P-7007 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | IRGD-7007 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3782 | 4 | 7000 | IRGD-7007 | IRGAH-7007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL |  | 10
3783 | 4 | 7000 | IRGD-7007 | IRGAHH7007 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | %LFL | 25
3784 | 4 | 7000 | IRGD-7007 | XA-7011 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3785 | 3 | 7000 | TGD-7001 | TGD-7001 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3786 | 3 | 7000 | TGD-7001 | TGAH-7001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3787 | 3 | 7000 | TGD-7001 | TGAHH-7001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3788 | 3 | 7000 | TGD-7001 | XA-7005 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3789 | 3 | 7000 | TGD-7002 | TGD-7002 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3790 | 3 | 7000 | TGD-7002 | TGAH-7002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3791 | 3 | 7000 | TGD-7002 | TGAHH-7002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3792 | 3 | 7000 | TGD-7002 | XA-7006 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3793 | 3 | 7000 | TGD-7003 | TGD-7003 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3794 | 3 | 7000 | TGD-7003 | TGAH-7003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3795 | 3 | 7000 | TGD-7003 | TGAHH-7003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3796 | 3 | 7000 | TGD-7003 | XA-7007 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3797 | 3 | 7000 | TGD-7004 | TGD-7004 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3798 | 3 | 7000 | TGD-7004 | TGAH-7004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3799 | 3 | 7000 | TGD-7004 | TGAHH-7004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3800 | 3 | 7000 | TGD-7004 | XA-8008 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3801 | 4 | 7000 | TGD-7005 | TGD-7005 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7005 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3802 | 4 | 7000 | TGD-7005 | TGAH-7005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3803 | 4 | 7000 | TGD-7005 | TGAHH-7005 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3804 | 4 | 7000 | TGD-7005 | XA-8012 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3805 | 4 | 7000 | TGD-7006 | TGD-7006 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7006 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3806 | 4 | 7000 | TGD-7006 | TGAH-7006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3807 | 4 | 7000 | TGD-7006 | TGAHH-7006 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3808 | 4 | 7000 | TGD-7006 | XA-8013 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3809 | 4 | 7000 | TGD-7007 | TGD-7007 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0027 | AIR | NIS | LFAP |  | d | AM | TGD-7007 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3810 | 4 | 7000 | TGD-7007 | TGAH-7007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) |  | 50
3811 | 4 | 7000 | TGD-7007 | TGAHH-7007 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0010 | [5 empty] | AM | [10 empty] | (TLV-TWA) | 100
3812 | 4 | 7000 | TGD-7007 | XA-804 |  |  | Fault | ESBR-HS-CAF-0010 | DI | NIS | LFAP |  | d | AM | XA-7014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3813 | 3 | 7000 | SD-7000 | SA/HA-7000 | Status signal to FGS |  |  | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3814 | 3 | 7000 | TGD-7000 | TGA-7000 | Status signal to FGS |  |  | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3815 | 3 | 7000 | MCP-7000 | MCP-7000 | Status signal to FGS |  |  | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3816 | 3 | 7000 | IRGD-7000 | IRGA-7000 | Status signal to FGS |  |  | ESBR-HS-CAF-0010 | DO | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3817 | 3 | 7000 | UK-7000 | UK-7000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3818 | 3 | 7000 | UK-7000 | UK-7000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3819 | 3 | 7000 | UK-7000 | UK-7000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3820 | 4 | 7000 | UL-7000 | UL-7000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3821 | 4 | 7000 | UL-7000 | UL-7000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3822 | 4 | 7000 | UL-7000 | UL-7000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6
3823 | 4 | 7000 | SD-7012 | SD-7012 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3824 | 4 | 7000 | SD-7012 | SD-7010 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3825 | 4 | 7000 | SD-7012 | SD-7008 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3826 | 4 | 7000 | SD-7012 | SD-7007 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3827 | 4 | 7000 | SD-7012 | SD-7009 | Electrical room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3828 | 4 | 7000 | SD-7012 | SD-7014 | HVAC |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3829 | 4 | 7000 | SD-7012 | SD-7017 | Staff |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3830 | 4 | 7000 | SD-7012 | SD-7015 | Washing Area |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3831 | 4 | 7000 | SD-7012 | SD-7001 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3832 | 4 | 7000 | SD-7012 | SD-7002 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3833 | 4 | 7000 | SD-7012 | SD-7003 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3834 | 4 | 7000 | SD-7012 | SD-7006 | Service Area |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3835 | 4 | 7000 | SD-7012 | SD-7005 | VIP Dinning Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3836 | 4 | 7000 | SD-7012 | SD-7004 | VIP Dinning Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3837 | 4 | 7000 | SD-7012 | SD-7016 | …….. |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3838 | 4 | 7000 | SD-7012 | HDROR-7001 | Pantry |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | HDROR-7001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3839 | 4 | 7000 | MCP-7012 | MCP-7012 | Corridor Second floor |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | MCP-7012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3840 | 4 | 7000 | MCP-7012 | MCP-7005 | VIP Dinning Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | MCP-7005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3841 | 4 | 7000 | MCP-7012 | MCP-7006 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | MCP-7006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3842 | 4 | 7000 | MCP-7012 | MCP-7008 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | MCP-7008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3843 | 4 | 7000 | MCP-7012 | MCP-7009 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | MCP-7009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3844 | 4 | 7000 | MCP-7012 | MCP- 701 1 | Corridor Second floor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | MCP- 701 1 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3845 | 4 | 7000 | MCP-7012 | MCP-7010 | Corridor Second floor |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | MCP-7010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3846 | 4 | 7000 | SD-7067 | SD-7067 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7067 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3847 | 4 | 7000 | SD-7067 | SD-7044 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7044 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3848 | 4 | 7000 | SD-7067 | SD-7042 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7042 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3849 | 4 | 7000 | SD-7067 | SD-7040 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7040 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3850 | 4 | 7000 | SD-7067 | SD-7039 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7039 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3851 | 4 | 7000 | SD-7067 | SD-7041 | Electrical room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7041 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3852 | 4 | 7000 | SD-7067 | SD-7049 | Staff |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7049 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3853 | 4 | 7000 | SD-7067 | SD-7047 | Washing Area |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7047 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3854 | 4 | 7000 | SD-7067 | SD-7065 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7065 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3855 | 4 | 7000 | SD-7067 | SD-7048 | Kitchen Manager Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7048 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3856 | 4 | 7000 | SD-7067 | SD-7066 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7066 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3857 | 4 | 7000 | SD-7067 | SD-7038 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7038 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3858 | 4 | 7000 | SD-7067 | SD-7033 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7033 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3859 | 4 | 7000 | SD-7067 | SD-7034 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7034 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3860 | 4 | 7000 | SD-7067 | SD-7035 | Dinnig Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7035 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3861 | 4 | 7000 | SD-7067 | SD-7037 | VIP Dinning Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7037 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3862 | 4 | 7000 | SD-7067 | SD-7036 | VIP Dinning Hall |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7036 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3863 | 4 | 7000 | SD-7063 | SD-7063 | Security Management |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7063 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3864 | 4 | 7000 | SD-7063 | SD-7062 | Security CCTV Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7062 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3865 | 4 | 7000 | SD-7063 | SD-7061 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7061 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3866 | 4 | 7000 | SD-7063 | SD-7068 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7068 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3867 | 4 | 7000 | SD-7063 | SD-7064 | Copr Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7064 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3868 | 4 | 7000 | SD-7063 | SD-7069 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7069 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3869 | 4 | 7000 | SD-7063 | SD-7060 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7060 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3870 | 4 | 7000 | SD-7063 | SD-7059 | Plant management Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7059 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3871 | 4 | 7000 | SD-7063 | SD-7058 | Confrance Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7058 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3872 | 4 | 7000 | SD-7063 | SD-7054 | Management Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7054 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3873 | 4 | 7000 | SD-7063 | SD-7053 | Management Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7053 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3874 | 4 | 7000 | SD-7063 | SD-7052 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7052 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3875 | 4 | 7000 | SD-7063 | SD-7051 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7051 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3876 | 4 | 7000 | SD-7063 | SD-7050 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7050 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3877 | 4 | 7000 | SD-7063 | SD-7057 | Female Paryer Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7057 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3878 | 4 | 7000 | SD-7063 | SD-7056 | Mail Prayer Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7056 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3879 | 4 | 7000 | SD-7063 | SD-7073 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7073 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3880 | 4 | 7000 | SD-7063 | SD-7055 | Archive |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7055 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3881 | 4 | 7000 | SD-7063 | SD-7071 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7071 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3882 | 4 | 7000 | SD-7063 | SD-7072 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7072 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3883 | 4 | 7000 | SD-7063 | SD-7070 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7070 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3884 | 4 | 7000 | SD-7031 | SD-7031 | Security Management |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7031 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3885 | 4 | 7000 | SD-7031 | SD-7030 | Security CCTV Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7030 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3886 | 4 | 7000 | SD-7031 | SD-7029 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7029 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3887 | 4 | 7000 | SD-7031 | HDROR-7007 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | HDROR-7007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3888 | 4 | 7000 | SD-7031 | SD-7032 | Copr Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7032 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3889 | 4 | 7000 | SD-7031 | SD-7028 | Corridor |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7028 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3890 | 4 | 7000 | SD-7031 | SD-7027 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7027 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3891 | 4 | 7000 | SD-7031 | SD-7026 | Plant management Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7026 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3892 | 4 | 7000 | SD-7031 | SD-7022 | Confrance Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7022 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3893 | 4 | 7000 | SD-7031 | SD-7021 | Management Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7021 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3894 | 4 | 7000 | SD-7031 | SD-7020 | Management Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7020 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3895 | 4 | 7000 | SD-7031 | SD-7019 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7019 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3896 | 4 | 7000 | SD-7031 | SD-7018 | Office |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3897 | 4 | 7000 | SD-7031 | SD-7025 | Female Paryer Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7025 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3898 | 4 | 7000 | SD-7031 | SD-7024 | Mail Prayer Room |  |  | ESBR-HS-LYT-0027 | AL | NIS |  |  |  |  | SD-7024 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3899 | 4 | 7000 | SD-7031 | SD-7023 | Archive |  |  | ESBR-HS-LYT-0027 | AL | NIS | LFAP |  | SF | AM | SD-7023 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3900 | 3 | 7000 | UK-7001 | UK-7001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3901 | 3 | 7000 | UK-7001 | UK-7001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3902 | 3 | 7000 | UK-7001 | UK-7001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3903 | 4 | 7000 | UL-7001 | UL-7001A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3904 | 4 | 7000 | UL-7001 | UL-7001B |  | Clean Agent System,MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3905 | 4 | 7000 | UL-7001 | UL-7001C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3906 | 3 | 7000 | UK-7002 | UK-7002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3907 | 3 | 7000 | UK-7002 | UK-7002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3908 | 3 | 7000 | UK-7002 | UK-7002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3909 | 4 | 7000 | UL-7002 | UL-7002A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3910 | 4 | 7000 | UL-7002 | UL-7002B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3911 | 4 | 7000 | UL-7002 | UL-7002C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3912 | 3 | 7000 | UK-7003 | UK-7003A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3913 | 3 | 7000 | UK-7003 | UK-7003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3914 | 3 | 7000 | UK-7003 | UK-7003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3915 | 4 | 7000 | UL-7003 | UL-7003A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3916 | 4 | 7000 | UL-7003 | UL-7003B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3917 | 4 | 7000 | UL-7003 | UL-7003C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3918 | 3 | 7000 | UK-7004 | UK-7004A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3919 | 3 | 7000 | UK-7004 | UK-7004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3920 | 3 | 7000 | UK-7004 | UK-7004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3921 | 4 | 7000 | UL-7004 | UL-7004A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3922 | 4 | 7000 | UL-7004 | UL-7004B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3923 | 4 | 7000 | UL-7004 | UL-7004C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3924 | 3 | 7000 | UK-7005 | UK-7005A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3925 | 3 | 7000 | UK-7005 | UK-7005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3926 | 3 | 7000 | UK-7005 | UK-7005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3927 | 4 | 7000 | UL-7005 | UL-7005A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3928 | 4 | 7000 | UL-7005 | UL-7005B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3929 | 4 | 7000 | UL-7005 | UL-7005C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0027 | DO | NIS | LFAP |  | d | AM | 7000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On hold
3930 | 3 | 7000 | MCP-7001 | MCP-7001 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0027 | DIR | NIS | LFAP |  | d | AM | 7000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
3931 | 3 | 7000 | MCP-7002 | MCP-7002 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0027 | DIR | NIS | LFAP |  | d | AM | 7000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
3932 | 3 | 7000 | MCP-7003 | MCP-7003 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0027 | DIR | NIS | LFAP |  | d | AM | 7000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
3933 | 3 | 7000 | MCP-7004 | MCP-7004 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0027 | DIR | NIS | LFAP |  | d | AM | 7000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
3934 | 4 | 7000 | LFAP-7000 | LFXA-7000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-6 | ESBR-CI-DAS-0030
3935 | 4 | 7000 | LFAP-7000 | LFXF-7000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-7000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
3936 | 4 | 7000 | HVAC-7000 | MHKL-Y7000 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0009 | DOR | NIS | LFAP |  |  | CCR | HVAC7000 | 1 | 08-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3937 | 4 | 7000 | HVAC-7000 | XL-Y7000 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0009 | DIR | NIS | LFAP |  |  | CCR | HVAC7000 | 2 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3938 | 4 | 7000 | HVAC-7000 | HVAC-Y7000 |  |  | HVAC Shutdown singnal | ESBR-HS-CAF-0009 | DIR | NIS | LFAP |  |  | WH | HVAC7000 | 3 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3939 | 4 | 7000 | HVAC-7000 | HVAC-7000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0009 | DO | NIS | LFAP | CRR |  | FGDS | CAP-7000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3940 | 4 | 8000 | HVAC-8000 | MHKL-Y8000 | Shutdown all HVAC System & Dampers Close of Sub station |  | HVAC signals | ESBR-HS-CAF-0010 | DOR | NIS | LFAP |  |  | CCR | HVAC8000 | 1 | 08-P-1.50-11-NAR-R-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3941 | 4 | 8000 | HVAC-8000 | XL-Y8000 | HVAC status |  | HVAC signals | ESBR-HS-CAF-0010 | DIR | NIS | LFAP |  |  | CCR | HVAC8000 | 2 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3942 | 4 | 8000 | HVAC-8000 | HVAC-Y8000 |  |  | HVAC Shutdown singnal | ESBR-HS-CAF-0010 | DIR | NIS | LFAP |  |  | WH | HVAC8000 | 3 | 08-P-1.50-11-NAR-R-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3943 | 4 | 8000 | HVAC-8000 | HVAC-8000A | HVAC status |  | HVAC signals to FGS | ESBR-HS-CAF-0010 | DO | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 5 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-8 | ESBR-CI-DAS-0030 |  |  | ON HOLD, Signals will be modified based on vendor data
3944 | 3 | 8000 | IRGD-8001 | IRGD/P-8001 | AIR LOCK | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | IRGD-8001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3945 | 3 | 8000 | IRGD-8001 | IRGAH-8001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL |  | 10
3946 | 3 | 8000 | IRGD-8001 | IRGAHH8001 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL | 25
3947 | 3 | 8000 | IRGD-8001 | XA-8001 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3948 | 3 | 8000 | IRGD-8002 | IRGD/P-8002 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | IRGD-8002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3949 | 3 | 8000 | IRGD-8002 | IRGAH-8002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL |  | 10
3950 | 3 | 8000 | IRGD-8002 | IRGAHH8002 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL | 25
3951 | 3 | 8000 | IRGD-8002 | XA-8002 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3952 | 3 | 8000 | IRGD-8003 | IRGD/P-8003 | HVAC ROOM | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | IRGD-8003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3953 | 3 | 8000 | IRGD-8003 | IRGAH-8003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL |  | 10
3954 | 3 | 8000 | IRGD-8003 | IRGAHH8003 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL | 25
3955 | 3 | 8000 | IRGD-8003 | XA-8003 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3956 | 3 | 8000 | IRGD-8004 | IRGD/P-8004 | HVAC ROOM Inside Canale | Point Type Gas Detector | Flammable. Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | IRGD-8004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | %LFL | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3957 | 3 | 8000 | IRGD-8004 | IRGAH-8004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH LEVEL 25% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL |  | 10
3958 | 3 | 8000 | IRGD-8004 | IRGAHH8004 | (GREEN FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | IRGD HIGH HIGH LEVEL 50% OF LFL | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | %LFL | 25
3959 | 3 | 8000 | IRGD-8004 | XA-8004 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3960 | 3 | 8000 | TGD-8001 | TGD-8001 | AIR LOCK |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | TGD-8001 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3961 | 3 | 8000 | TGD-8001 | TGAH-8001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) |  | 50
3962 | 3 | 8000 | TGD-8001 | TGAHH-8001 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) | 100
3963 | 3 | 8000 | TGD-8001 | XA-8005 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3964 | 3 | 8000 | TGD-8002 | TGD-8002 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | TGD-8002 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3965 | 3 | 8000 | TGD-8002 | TGAH-8002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) |  | 50
3966 | 3 | 8000 | TGD-8002 | TGAHH-8002 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) | 100
3967 | 3 | 8000 | TGD-8002 | XA-8006 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8006 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3968 | 3 | 8000 | TGD-8003 | TGD-8003 | HVAC ROOM |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | TGD-8003 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3969 | 3 | 8000 | TGD-8003 | TGAH-8003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) |  | 50
3970 | 3 | 8000 | TGD-8003 | TGAHH-8003 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) | 100
3971 | 3 | 8000 | TGD-8003 | XA-8007 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3972 | 3 | 8000 | TGD-8004 | TGD-8004 | HVAC ROOM Inside canale |  | Toxic Gas (Sub station) | ESBR-HS-LYT-0024 | AIR | NIS | LFAP |  | d | FB | TGD-8004 |  | 01-T-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc |  |  | 0 | 100 | (TLV-TWA) | [5 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030 |  |  | 3 Wire, 0-20 mA
3973 | 3 | 8000 | TGD-8004 | TGAH-8004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH LEVEL 10 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) |  | 50
3974 | 3 | 8000 | TGD-8004 | TGAHH-8004 | (YELLOW FLASHING LIGHT) | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | TGD HIGH HIGH LEVEL 50 PPM | ESBR-HS-CAF-0009 | [5 empty] | FB | [10 empty] | (TLV-TWA) | 100
3975 | 3 | 8000 | TGD-8004 | XA-8008 |  |  | Fault | ESBR-HS-CAF-0009 | DI | NIS | LFAP |  | d | FB | XA-8008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/38-1 | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-4 | ESBR-CI-DAS-0030
3976 | 3 | 8000 | SD-8000 | SA/HA-8000 | Status signal to FGS |  |  | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 1 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
3977 | 3 | 8000 | TGD-8000 | TGA-8000 | Status signal to FGS |  |  | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 2 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
3978 | 3 | 8000 | MCP-8000 | MCP-8000 | Status signal to FGS |  |  | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 3 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
3979 | 3 | 8000 | IRGD-8000 | IRGA-8000 | Status signal to FGS |  |  | ESBR-HS-CAF-0009 | DO | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 4 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
3980 | 3 | 8000 | UK-8001 | UK-8001A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3981 | 3 | 8000 | UK-8001 | UK-8001B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3982 | 3 | 8000 | UK-8001 | UK-8001C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3983 | 4 | 8000 | UL-8001 | UL-8001A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3984 | 4 | 8000 | UL-8001 | UL-8001B |  | Clean Agent System,MCP/Fire | (RED FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3985 | 4 | 8000 | UL-8001 | UL-8001C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND70 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3986 | 3 | 8000 | UK-8002 | UK-8002A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3987 | 3 | 8000 | UK-8002 | UK-8002B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3988 | 3 | 8000 | UK-8002 | UK-8002C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3989 | 4 | 8000 | UL-8002 | UL-8002A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3990 | 4 | 8000 | UL-8002 | UL-8002B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3991 | 4 | 8000 | UL-8002 | UL-8002C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND71 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3992 | 3 | 8000 | UK-8003 | UK-8003A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3993 | 3 | 8000 | UK-8003 | UK-8003B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3994 | 3 | 8000 | UK-8003 | UK-8003C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
3995 | 4 | 8000 | UL-8003 | UL-8003A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3996 | 4 | 8000 | UL-8003 | UL-8003B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3997 | 4 | 8000 | UL-8003 | UL-8003C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND72 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3998 | 3 | 8000 | UK-8004 | UK-8004A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
3999 | 3 | 8000 | UK-8004 | UK-8004B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4000 | 3 | 8000 | UK-8004 | UK-8004C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4001 | 4 | 8000 | UL-8004 | UL-8004A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
4002 | 4 | 8000 | UL-8004 | UL-8004B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4003 | 4 | 8000 | UL-8004 | UL-8004C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND73 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On hold
4004 | 3 | 8000 | UK-8005 | UK-8005A | AUDIBLE ALARM (CONTINUOUS ) | Clean Agent System,MCP | A quad cable has been considered for this device | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 1,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4005 | 3 | 8000 | UK-8005 | UK-8005B | AUDIBLE ALARM (INTERMITTENT-(LONG-SHORT) ) | (25% LFL) or (50% LFL) IRGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 2,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4006 | 3 | 8000 | UK-8005 | UK-8005C | AUDIBLE ALARM (INTERMITTENT-(DOUBLE LONG) ) | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | HOOTER | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 3,3 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/46 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4007 | 4 | 8000 | UL-8005 | UL-8005A |  | (10 ppm Poiseness Gas) or (50 ppm Poiseness Gas) TGD | (YELLOW FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 5 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
4008 | 4 | 8000 | UL-8005 | UL-8005B |  | Clean Agent System,MCP | (RED FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 6 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030
4009 | 4 | 8000 | UL-8005 | UL-8005C |  | (25% LFL) or (50% LFL) IRGD | (GREEN FLASHING LIGHT) | ESBR-HS-LYT-0024 | DO | NIS | LFAP |  | d | FB | 8000JND74 | 7 | 16-C-2.50-01-SWA-S-RD-N |  | ESBR-CI-DGR-0010/45 | SYS/24Vdc | CLOSE | [9 empty] | ESBR-CI-DWG-0002-1 | ESBR-CI-DAS-0030 |  |  | On Hold
4010 | 4 | 8000 | LFAP-8000 | LFXF-8000 | Signal to FGS |  | FAP Cumilitive Alarm | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 6 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4011 | 4 | 8000 | LFAP-8000 | LFXA-8000 | Signal to FGS |  | FAP Cumilitive Fault | ESBR-CI-JSD-0008 | DOR | NIS | FGDS | CRR |  | LFAP | CAP-8000 | 7 | 16-P-1.50-11-SWA-S-RD-N |  |  | EXT/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4012 | 3 | 8000 | MCP-8001 | MCP-8001 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0024 | DIR | NIS | LFAP |  | d | FB | 8000JND70 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
4013 | 3 | 8000 | MCP-8002 | MCP-8002 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0024 | DIR | NIS | LFAP |  | d | FB | 8000JND71 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
4014 | 3 | 8000 | MCP-8003 | MCP-8003 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0024 | DIR | NIS | LFAP |  | d | FB | 8000JND72 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
4015 | 3 | 8000 | MCP-8004 | MCP-8004 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0024 | DIR | NIS | LFAP |  | d | FB | 8000JND73 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
4016 | 3 | 8000 | MCP-8005 | MCP-8005 | OUTSIDE AREA | (RED FLASHING LIGHT) | MANUAL CALL POINT | ESBR-HS-LYT-0024 | DIR | NIS | LFAP |  | d | FB | 8000JND74 | 8 | 16-C-2.50-01-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN
4017 | 3 | 8000 | UK-8000 | UK-8000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 9 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4018 | 3 | 8000 | UK-8000 | UK-8000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 10 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4019 | 3 | 8000 | UK-8000 | UK-8000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 11 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4020 | 3 | 8000 | UL-8000 | UL-8000A | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 12 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4021 | 3 | 8000 | UL-8000 | UL-8000B | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 13 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4022 | 3 | 8000 | UL-8000 | UL-8000C | Signal from FGS |  | Activation alarm from F&G |  | DI | NIS | LFAP | CRR |  | FGDS | CAP-8000 | 14 | 16-P-1.50-11-SWA-S-RD-N |  |  | SYS/24Vdc | OPEN | [9 empty] | ESBR-CI-DWG-0002-7
4023 | 4 | 8000 | SD-8018 | SD-8018 | Control Room |  |  | ESBR-HS-LYT-0024 | AL | NIS | LFAP |  | SF | FB | SD-8018 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4024 | 4 | 8000 | SD-8018 | SD-8023 |  |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8023 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4025 | 4 | 8000 | SD-8018 | SD-8019 | Sport Club |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8019 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4026 | 4 | 8000 | SD-8018 | SD-8021 | Safety Foreman |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8021 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4027 | 4 | 8000 | SD-8018 | SD-8020 | Safety Foreman |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8020 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4028 | 4 | 8000 | SD-8018 | SD-8024 |  |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8024 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4029 | 4 | 8000 | SD-8018 | SD-8025 |  |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8025 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4030 | 4 | 8000 | SD-8018 | SD-8012 | Duty Room |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8012 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4031 | 4 | 8000 | SD-8018 | SD-8022 | Corridor |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8022 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4032 | 4 | 8000 | SD-8018 | SD-8016 | Doctor Room |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8016 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4033 | 4 | 8000 | SD-8018 | SD-8017 | Electrical Room |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8017 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4034 | 4 | 8000 | SD-8018 | SD-8015 | Waiting Area |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8015 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4035 | 4 | 8000 | SD-8018 | SD-8014 | First Aid room |  |  | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8014 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4036 | 4 | 8000 | SD-8018 | SD-8013 | Fire Fighting Room |  |  | ESBR-HS-LYT-0024 | AL | NIS | LFAP |  | SF | FB | SD-8013 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4037 | 4 | 8000 | SD-8008 | SD-8008 | Control Room | SD-8002 | Duty Room | ESBR-HS-LYT-0024 | AL | NIS | LFAP |  | SF | FB | SD-8008 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4038 | 4 | 8000 | SD-8008 | SD-8010 | Safety Foreman | SD-8012 | Duty Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8010 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4039 | 4 | 8000 | SD-8008 | SD-8009 | Sport Club | SD-8022 | Corridor | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8009 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4040 | 4 | 8000 | SD-8008 | SD-8011 | Safety Foreman | HDROR-8001 | Pantry | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8011 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4041 | 4 | 8000 | SD-8008 | SD-8026 | Office | SD-8006 | Doctor Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8026 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4042 | 4 | 8000 | SD-8008 | HDROR-8002 | Kitchen Second Floor | SD-8016 | Doctor Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | HDROR-8002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4043 | 4 | 8000 | SD-8008 | SD-8001 |  | SD-8017 | Electrical Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4044 | 4 | 8000 | SD-8008 | SD-8003 | Fire Fighting Room | SD-8007 | Electrical Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8003 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4045 | 4 | 8000 | SD-8008 | SD-8004 | First Aid room | SD-8015 | Waiting Area | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8004 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4046 | 4 | 8000 | SD-8008 | SD-8005 | Waiting Area | SD-8005 | Waiting Area | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8005 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4047 | 4 | 8000 | SD-8008 | SD-8007 | Electrical Room | SD-8004 | First Aid room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-8007 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4048 | 4 | 8000 | SD-8008 | SD-8006 | Doctor Room | SD-8014 | First Aid room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | SD-806 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4049 | 4 | 8000 | SD-8008 | HDROR-8001 | Pantry | SD-8013 | Fire Fighting Room | ESBR-HS-LYT-0024 | AL | NIS |  |  |  |  | HDROR-8001 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030
4050 | 4 | 8000 | SD-8008 | SD-8002 | Duty Room | SD-8003 | Fire Fighting Room | ESBR-HS-LYT-0024 | AL | NIS | LFAP |  | SF | FB | SD-8002 |  | 01-P-1.50-01-NAR-S-RD-N |  | ESBR-CI-DGR-0010/44/48 | SYS/24Vdc |  |  | 0 | 100 | % | [5 empty] | ESBR-CI-DWG-0002-7 | ESBR-CI-DAS-0030